Table of Contents

Cover Sheet	2

Vessel Design Summary:	3

Nozzle Summary:	6

Nozzle Schedule:	7

Bill of Material:	8

MDMT Summary:	9

Warnings and Errors:	11

Input Echo:	12

XY Coordinate Calculations:	22

Flg Calc [Int P]:   CH. FLANGE	23

Flg Calc [Int P]:   SH. FLANGE	28

Internal Pressure Calculations:	33

External Pressure Calculations:	40

Element and Detail Weights:	41

Nozzle Flange MAWP:	44

Wind Load Calculation:	45

Earthquake Load Calculation:	46

Center of Gravity Calculation:	48

Saddle Calcs: Operating Case:	49

Saddle Calcs: Test Case:	65

Conical Section:   SH. Cone	79

Nozzle Calcs.:  T1 (3in.)	84

Nozzle Calcs.:  T2 (3in.)	89

Nozzle Calcs.:  S1 (4in.)	94

Nozzle Calcs.:  S2 (6in.)	100

Nozzle Calcs.:  V (2in.)	110

Nozzle Calcs.:  D (2in.)	113

Nozzle Calcs.:  PSV (3in.)	116

Nozzle Calcs.:  LG1 (2in.)	120

Nozzle Calcs.:  LG2 (2in.)	123

ASME TS Calc: DESIGN	126

ASME TS Calc: MDMT	134

ASME TS Calc: HYDROTEST	139

Hydrotest for CH. Body Flange	144

Hydrotest for SH. Body Flange	149

FEA for Nozzles T1 & T2 (3in.)	154

FEA for Nozzle S1 (4in.)	174

DESIGN CALCULATION

In Accordance with ASME Section VIII Division 1

ASME Code Version     : 2019

Analysis Performed by : #Replace this text with your company name and th

Job File              : D:\JAM-PETROELECTRIC\Chiller-Rev.00

Date of Analysis      : Apr 17,2024   11:12am

PV Elite 23, January 2021

Vessel Design Summary:

ASME Code, Section VIII Division 1, 2019

Diameter Spec : 600.000 x 600.000 x 925.000 mm. ID

Vessel Design Length, Tangent to Tangent           3563.53  mm.

Specified Datum Line Distance                         0.00  mm.

Shell  Side  Design Temperature                        120  °C

Channel Side Design Temperature                         85  °C

Shell  Side  Design Pressure                        22.000  bars

Channel Side Design Pressure                         6.800  bars

Shop Shell Side Test Pressure                       28.600  bars

Shop Channel Side Test Pressure                      8.840  bars

Wind Design Code                                       UBC

Earthquake Design Code                              UBC-97

Materials of Construction:

Component |                 |       |                        |         |Normal |  Impact |

Type |        Material | Class |              Thickness |   UNS # |  ized |  Tested |

----------------------------------------------------------------------------------------------

Shell |       SA-516 70 |   ... |                    ... |  K02700 |   Yes |      No |

Head |       SA-516 70 |   ... |                    ... |  K02700 |   Yes |      No |

Cone |       SA-516 70 |   ... |                    ... |  K02700 |   Yes |      No |

Flange |        SA-266 2 |   ... |                    ... |  K03506 |    No |      No |

Flange |      SA-350 LF2 |     1 |                    ... |  K03011 |    No |     Yes |

Nozzle |        SA-106 B |   ... |                    ... |  K03006 |    No |      No |

Nozzle |        SA-333 6 |   ... |                    ... |  K03006 |    No |     Yes |

Nozzle |      SA-350 LF2 |     1 |                    ... |  K03011 |    No |     Yes |

Re-Pad |       SA-516 70 |   ... |                    ... |  K02700 |   Yes |      No |

Nozzle Flg |          SA-105 |   ... |                    ... |  K03504 |    No |      No |

Nozzle Flg |      SA-350 LF2 |     1 |                    ... |  K03011 |    No |     Yes |

Tubes |        SA-334 6 |   ... |                    ... |  K03006 |    No |     Yes |

Tubesheet |      SA-350 LF2 |     1 |                    ... |  K03011 |    No |     Yes |

Flg Bolting |       SA-193 B7 |   ... |               <= 2 1/2 |  G41400 |    No |      No |

Hrz Bolting |       SA-193 B7 |   ... |               <= 2 1/2 |  G41400 |    No |      No |

Normalized is determined based on the UCS-66 material curve selection and Figure UCS-66.

Impact Tested is based on material selection and material data properties.

Element Pressures and MAWP (bars & mm.):

|        Design |         |           |             | Str. |    In |

Element Description |      Pressure |    Ext. |   Element |   Corrosion | Flg. | Creep |

or Type |  + Stat. head |  Press. |   M.A.W.P |   Allowance | Gov. | Range |

--------------------------------------------------------------------------------------------

CH. Head |         6.854 |    1.00 |    32.100 |      3.0000 |   No |    No |

CH. Barrel |         6.854 |    1.03 |    31.400 |      3.0000 |  N/A |    No |

CH. Flange |         6.854 |    1.03 |    14.600 |      3.0000 |  N/A |    No |

SH. Flange |        22.031 |    1.03 |    23.400 |      3.0000 |  N/A |    No |

Port Barrel |        22.032 |    1.03 |    40.200 |      3.0000 |  N/A |    No |

SH. Cone |        22.048 |    1.03 |    22.800 |      3.0000 |  N/A |    No |

SH. Barrel |        22.048 |    1.03 |    26.300 |      3.0000 |  N/A |    No |

SH. Head |        22.048 |    1.03 |    26.800 |      3.0000 |   No |    No |

Liquid Level: 925.00 mm.  Dens.: 0.001 kg./cm³     Sp. Gr.: 0.533

Element Types and Properties:

Element |"To" Elev |  Element |  Nominal | Finished | Reqd Thk | Reqd Thk |   Long |   Circ |

|          |   Length |Thickness |Thickness | Internal | External |    Eff |    Eff |

Type |      mm. |      mm. |      mm. |      mm. |      mm. |      mm. |        |        |

------------------------------------------------------------------------------------------------

Ellipse  |     50.0 |     50.0 |     12.0 |     10.0 |      4.5 |      4.6 |   1.00 |   1.00 |

Cylinder |    350.0 |    300.0 |     10.0 |     10.0 |      4.5 |      4.7 |   1.00 |   1.00 |

Body Flg |    435.0 |     85.0 |     90.0 |     60.0 |     58.2 |     57.3 |   1.00 |   1.00 |

Body Flg |    598.5 |     85.0 |     90.0 |     60.0 |     57.9 |     53.5 |   1.00 |   1.00 |

Cylinder |    748.5 |    150.0 |     12.0 |     12.0 |      7.9 |      4.1 |   1.00 |   1.00 |

Conical  |   1313.5 |    565.0 |     12.0 |     12.0 |     11.7 |      8.6 |   1.00 |   1.00 |

Cylinder |   3513.5 |   2200.0 |     12.0 |     12.0 |     10.5 |      7.8 |   1.00 |   1.00 |

Ellipse  |   3563.5 |     50.0 |     14.0 |     12.0 |     10.4 |      5.5 |   1.00 |   1.00 |

Saddle Parameters:

Saddle Width                                             140.000  mm.

Saddle Bearing Angle                                     120.000  deg.

Centerline Dimension                                     750.000  mm.

Wear Pad Width                                           300.000  mm.

Wear Pad Thickness                                        12.000  mm.

Wear Pad Bearing Angle                                   132.000  deg.

Distance from Saddle to Tangent                          800.000  mm.

Baseplate Length                                         900.000  mm.

Baseplate Thickness                                       15.000  mm.

Baseplate Width                                          170.000  mm.

Number of Ribs (including outside ribs)                        3

Rib Thickness                                             12.000  mm.

Web Thickness                                             12.000  mm.

Height of Center Web                                     367.500  mm.

Number of Bolts in Baseplate                                   4

Baseplate Sketch

|------------------- 900.000 mm. --------------------|

------------------------------------------------------ ---

|                                                    |

|                                                    | 170.000 mm.

|                                                    |

------------------------------------------------------ ---

Baseplate Plan View

------------------------------------------------------ ---

|                                                    | 15.000 mm.

------------------------------------------------------ ---

Baseplate Side View

Maximum Tensile Bolt Load                                    99.  Kgf

Summary of Maximum Saddle Loads, Operating Case:

Maximum Vertical Saddle Load                             4628.38  Kgf

Maximum Transverse Saddle Shear Load                      488.09  Kgf

Maximum Longitudinal Saddle Shear Load                    976.18  Kgf

Summary of Maximum Saddle Loads, Operating Case, Un-Factored:

Maximum Vertical Saddle Load                             5186.93  Kgf

Maximum Transverse Saddle Shear Load                     1303.28  Kgf

Maximum Longitudinal Saddle Shear Load                   1394.54  Kgf

Summary of Maximum Saddle Loads, Hydrotest Case :

Maximum Vertical Saddle Load                             4000.46  Kgf

Maximum Transverse Saddle Shear Load                       78.72  Kgf

Maximum Longitudinal Saddle Shear Load                     37.89  Kgf

Local Stress Analysis Results:

|        Analysis |    Max Stress |   High Stress |          Pass |

Description |            Type |         Ratio |      Location |          Fail |

------------------------------------------------------------------------------------

S2 (6in.) |     WRC-107/537 |         0.833 |           n/a |        Passed |

Weights:

Fabricated - Bare  W/O Removable Internals                2856.3  kg.

Shop Test  - Fabricated + Water ( Full )                  4882.9  kg.

Shipping   - Fab. + Rem. Intls.+ Shipping App.            2856.3  kg.

Erected    - Fab. + Rem. Intls.+ Insul. (etc)             3029.6  kg.

Empty      - Fab. + Intls. + Details + Wghts.             3029.6  kg.

Operating  - Empty + Operating Liquid (No CA)             4256.0  kg.

Field Test - Empty Weight + Water (Full)                  4815.0  kg.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Nozzle Calculation Summary:

Description        |       MAWP |    Ext |      MAPNC | UG-45    [tr] |    Weld |   Areas or |

|       bars |        |       bars |       |   mm. |    Path |   Stresses |

----------------------------------------------------------------------------------------------

T1 (3in.)          |       16.6 |    ... |        ... |    OK |  4.50 |     OK  | No Calc[*] |

T1 (3in.)          |       16.6 |    ... |        ... |    OK |  4.50 |     OK  | No Calc[*] |

T2 (3in.)          |       16.6 |    ... |        ... |    OK |  4.51 |     OK  | No Calc[*] |

T2 (3in.)          |       16.6 |    ... |        ... |    OK |  4.51 |     OK  | No Calc[*] |

S1 (4in.)          |       22.8 |     OK |        ... |    OK |  8.26 |     OK  |     Passed |

S2 (6in.)          |       26.3 |     OK |        ... |    OK |  9.22 |     OK  |     Passed |

V (2in.)           |       26.3 |    ... |        ... |    OK |  7.80 |     OK  | No Calc[*] |

D (2in.)           |       26.3 |    ... |        ... |    OK |  7.80 |     OK  | No Calc[*] |

PSV (3in.)         |       26.3 |    ... |        ... |    OK |  7.80 |     OK  | No Calc[*] |

LG1 (2in.)         |       26.3 |    ... |        ... |    OK |  6.42 |     OK  | No Calc[*] |

LG2 (2in.)         |       26.3 |    ... |        ... |    OK |  6.42 |     OK  | No Calc[*] |

----------------------------------------------------------------------------------------------

Nozzle MAWP Summary:

Minimum MAWP Nozzles         :            22.8 Nozzle  : S1 (4in.)  [Shellside]

Minimum MAWP Nozzles         :            16.6 Nozzle  : T2 (3in.)  [Tubeside]

[*] - This was a small opening and the areas were not computed.

Note: MAWPs (Internal Case) shown above are at the High Point.

Check the Spatial Relationship between the Nozzles:

From Node | Nozzle Description | X Coordinate | Layout Angle |    Dia. Limit |

|                    |          mm. |          deg |           mm. |

------------------------------------------------------------------------------

20 |          T1 (3in.) |      200.000 |      108.819 |       163.130 |

20 |          T2 (3in.) |      200.000 |      251.181 |       163.130 |

60 |          S1 (4in.) |      898.525 |      270.000 |       201.662 |

70 |          S2 (6in.) |     2413.525 |       90.000 |       310.145 |

70 |           V (2in.) |     3363.526 |       90.000 |       113.600 |

70 |           D (2in.) |     3363.526 |      270.000 |       113.600 |

70 |         PSV (3in.) |     1483.525 |       90.000 |       150.862 |

70 |         LG1 (2in.) |     1913.525 |       90.000 |       102.068 |

70 |         LG2 (2in.) |     1913.525 |      270.000 |       102.068 |

The nozzle spacing is computed by the following:

= Sqrt( ll² + lc² ) where

ll - Arc length along the inside vessel surface in the long. direction.

lc - Arc length along the inside vessel surface in the circ. direction

If any interferences/violations are found, they will be noted below.

No interference violations have been detected!

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Nozzle Schedule:

Nominal or|   Schd|  Flg|  Nozzle|    Wall| Reinforcing Pad |    Cut|   Flg|

Actual| or FVC| Type|   O/Dia|     Thk| Diameter    Thk | Length| Class|

Description            Size|   Type|     |      in|      mm|              mm |     mm|      |

---------------------------------------------------------------------------------------------

V (2in.)        |  2.000 in|Actual |   LW|   3.307|  16.600|     ... |   ... |  213.9|   300|

D (2in.)        |  2.000 in|Actual |   LW|   3.307|  16.600|     ... |   ... |  213.9|   300|

LG1 (2in.)      |  2.000 in|   160 |   WN|   2.375|   8.738|     ... |   ... |  162.9|   300|

LG2 (2in.)      |  2.000 in|   160 |   WN|   2.375|   8.738|     ... |   ... |  162.9|   300|

T1 (3in.)       |  3.000 in|    80 |   WN|   3.500|   7.620|  190.00 | 10.00 |  230.4|   150|

T2 (3in.)       |  3.000 in|    80 |   WN|   3.500|   7.620|  190.00 | 10.00 |  230.4|   150|

PSV (3in.)      |  3.000 in|   160 |   WN|   3.500|  11.125|  190.00 | 12.00 |  214.1|   300|

S1 (4in.)       |  4.000 in|   120 |   WN|   4.500|  11.125|  220.00 | 12.00 |  196.8|   300|

S2 (6in.)       |  6.000 in|    80 |   WN|   6.625|  10.973|  300.00 | 12.00 |  199.7|   300|

General Notes for the above table:

The Cut Length is the Outside Projection + Inside Projection + Drop +

In Plane Shell Thickness.  This value does not include weld gaps,

nor does it account for shrinkage.

In the case of Oblique Nozzles, the Outside Diameter must

be increased.  The Re-Pad WIDTH  around the nozzle is calculated as follows:

Width of Pad = (Pad Outside Dia. (per above) - Nozzle Outside Dia.)/2

For hub nozzles, the thickness and diameter shown are those of the smaller

and thinner section.

Nozzle Material and Weld Fillet Leg Size Details (mm.):

|                    | Shl Grve | Noz Shl/Pad |    Pad OD |   Pad Grve |   Inside |

Description |           Material |     Weld |        Weld |      Weld |       Weld |     Weld |

-----------------------------------------------------------------------------------------------

V (2in.)    |         SA-350 LF2 |   12.000 |      10.000 |       ... |        ... |     ...  |

D (2in.)    |         SA-350 LF2 |   12.000 |      10.000 |       ... |        ... |     ...  |

LG1 (2in.)  |           SA-333 6 |   12.000 |      10.000 |       ... |        ... |     ...  |

LG2 (2in.)  |           SA-333 6 |   12.000 |      10.000 |       ... |        ... |     ...  |

T1 (3in.)   |           SA-106 B |   10.000 |      10.000 |     8.000 |     10.000 |     ...  |

T2 (3in.)   |           SA-106 B |   10.000 |      10.000 |     8.000 |     10.000 |     ...  |

PSV (3in.)  |           SA-333 6 |   12.000 |      10.000 |    10.000 |     12.000 |     ...  |

S1 (4in.)   |           SA-333 6 |   12.000 |      10.000 |    10.000 |     12.000 |     ...  |

S2 (6in.)   |           SA-333 6 |   12.000 |      10.000 |    10.000 |     12.000 |     ...  |

Note: The Outside projections below do not include the flange thickness.

Nozzle Miscellaneous Data:

|   Elev/Distance |   Layout |        Proj |    Proj |        Installed in |

Description      |      From Datum |    Angle |     Outside |  Inside |           Component |

|              mm.|      deg |          mm.|      mm.|                     |

---------------------------------------------------------------------------------------------

V (2in.)        |        3363.525 |     90.0 |      200.00 |    0.00 |          SH. Barrel |

D (2in.)        |        3363.525 |    270.0 |      200.00 |    0.00 |          SH. Barrel |

LG1 (2in.)      |        1913.525 |     90.0 |      150.00 |    0.00 |          SH. Barrel |

LG2 (2in.)      |        1913.525 |    270.0 |      150.00 |    0.00 |          SH. Barrel |

T1 (3in.)       |         200.000 |    108.8 |      200.00 |    0.00 |          CH. Barrel |

T2 (3in.)       |         200.000 |    251.2 |      200.00 |    0.00 |          CH. Barrel |

PSV (3in.)      |        1483.525 |     90.0 |      200.00 |    0.00 |          SH. Barrel |

S1 (4in.)       |         898.525 |    270.0 |      180.00 |    0.00 |            SH. Cone |

S2 (6in.)       |        2413.525 |     90.0 |      180.00 |    0.00 |          SH. Barrel |

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Bill of Materials:

QTY |                                                     DESCRIPTION |        MATERIAL |

-------------------------------------------------------------------------------------------

1 |   ELLIPTICAL HEAD: 2.0 X 1, 12.0mm. THK X 600.0mm. ID X 50.0mm. |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |                  CYLINDER: 10.0mm. THK X 600.0mm. ID X 300.0mm. |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |                          BODY FLANGE: 90.0mm. THK X 760.0mm. OD |        SA-266 2 |

-------------------------------------------------------------------------------------------

1 |                          BODY FLANGE: 90.0mm. THK X 760.0mm. OD |      SA-350 LF2 |

-------------------------------------------------------------------------------------------

1 |                  CYLINDER: 12.0mm. THK X 600.0mm. ID X 150.0mm. |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |                      CONE: 12.0mm. THK X 925.0mm. ID X 565.0mm. |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |                 CYLINDER: 12.0mm. THK X 925.0mm. ID X 2200.0mm. |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |   ELLIPTICAL HEAD: 2.0 X 1, 14.0mm. THK X 925.0mm. ID X 50.0mm. |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |                                    INSULATION: 200mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                    INSULATION: 300mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                     INSULATION: 85mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                     TUBESHEET: 650mm X 60mm THK |      SA-350 LF2 |

-------------------------------------------------------------------------------------------

376 |                              TUBES: 2500mm X 19mm DIA X 1mm THK |        SA-334 6 |

-------------------------------------------------------------------------------------------

1 |                                     INSULATION: 84mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                    INSULATION: 150mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                    INSULATION: 565mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

2 |                                         SADDLE: 140mm X 120 DEG |       SA-516 70 |

-------------------------------------------------------------------------------------------

1 |                                   INSULATION: 2200mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                    INSULATION: 281mm X 60mm THK |                 |

-------------------------------------------------------------------------------------------

1 |                                   GASKET: 650mm. OD X 624mm. ID |             ... |

-------------------------------------------------------------------------------------------

20 |                                    BODY FLANGE BOLTS: 22mm. DIA |       SA-193 B7 |

-------------------------------------------------------------------------------------------

40 |                           NUTS FOR BODY FLANGE BOLTS: 22mm. DIA |             ... |

-------------------------------------------------------------------------------------------

1 |                                                       NAMEPLATE |             ... |

-------------------------------------------------------------------------------------------

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Minimum Design Metal Temperature Results Summary :

Curve  Basic  Reduced  UG-20(f)  Thickness     Gov      E*   PWHT

Description               MDMT     MDMT      MDMT      ratio     Thk           reqd

Notes           °C       °C        °C                mm.

-----------------------------------------------------------------------------------

SH. Flange   [11]    !     -46      -46                0.566  12.000    1.00     No

Port Barrel   [8]    D     -48      -48       -29      0.562  12.000    1.00     No

SH. Cone      [8]    D     -48      -48       -29      0.998  12.000    1.00     No

SH. Barrel    [8]    D     -48      -48       -29      0.863  12.000    1.00     No

SH. Head     [10]    D     -48      -48       -29      0.849  12.000    1.00     No

SH. Head      [7]    D     -48      -48       -29      0.706  14.000    1.00     No

S1 (4in.)     [1]    D     -48      -48       -29      0.716  12.000    1.00     No

Nozzle Flg    [5]    !     -46      -89

S2 (6in.)     [1]    D     -48      -48       -29      0.833  12.000    1.00     No

Nozzle Flg    [5]    !     -46      -89

V (2in.)      [1]    D     -48      -48       -29      0.833  12.000    1.00     No

Nozzle Flg    [5]    !     -46      -46

D (2in.)      [1]    D     -48      -48       -29      0.835  12.000    1.00     No

Nozzle Flg    [5]    !     -46      -46

PSV (3in.)    [1]    D     -48      -48       -29      0.833  12.000    1.00     No

Nozzle Flg    [5]    !     -46      -89

LG1 (2in.)    [1]    D     -46     -104                0.104   7.645    1.00     No

Nozzle Flg    [5]    !     -46      -89

LG2 (2in.)    [1]    D     -46     -104                0.104   7.645    1.00     No

Nozzle Flg    [5]    !     -46      -89

Tubesheet: SS[13]    !     -46      -46                0.838  15.000    1.00     No

-----------------------------------------------------------------------------------

Warmest MDMT:              -46      -46

-----------------------------------------------------------------------------------

CH. Flange   [11]    C     -44      -48       -29      0.466  10.000    1.00     No

CH. Head     [10]    D     -48      -48       -29      0.454  10.000    1.00     No

CH. Head      [7]    D     -48      -48       -29      0.359  12.000    1.00     No

CH. Barrel    [8]    D     -48      -48       -29      0.462  10.000    1.00     No

T1 (3in.)     [1]    B      -8     -104       -29      0.070   6.668    1.00     No

Nozzle Flg    [5]    A     -18     -104

T2 (3in.)     [1]    B      -8     -104       -29      0.070   6.668    1.00     No

Nozzle Flg    [5]    A     -18     -104

Tubesheet: CS[14]    !     -46      -46                0.838  15.000    1.00     No

Bolting      [21]          -48

-----------------------------------------------------------------------------------

Warmest MDMT:               -8      -46

-----------------------------------------------------------------------------------

Exchanger Side        Computed MDMT      Required MDMT        Pass/Fail

°C                 °C

----------------------------------------------------------------------------

Shell                -46.0              -45.0             Pass

Channel/Tube                -46.0              -29.0             Pass

Notes:

[  ! ] - This was an impact tested material.

[  1] - Governing Nozzle Weld.

[  4] - ANSI Flange MDMT Calcs; Thickness ratio per UCS-66(b)(1)(-c).

[  5] - ANSI Flange MDMT Calcs; Thickness ratio per UCS-66(b)(1)(-b).

[  6] - MDMT Calculations at the Shell/Head Joint.

[  7] - MDMT Calculations for the Straight Flange.

[  8] - Cylinder/Cone/Flange Junction MDMT.

[  9] - Calculations in the Spherical Portion of the Head.

[10] - Calculations in the Knuckle Portion of the Head.

[11] - Calculated (Body Flange) Flange MDMT.

[12] - Calculated Flat Head MDMT per UCS-66.3

[13] - Tubesheet MDMT, shell side, if applicable

[14] - Tubesheet MDMT, tube side, if applicable

[15] - Nozzle Material

[16] - Shell or Head Material

[17] - Impact Testing required

[18] - Impact Testing not required, see UCS-66(b)(3)

[20] - Cylinder/Cone Junction MDMT based on Longitudinal Stress considerations

[21] - Body Flange Bolting Material

[22] - Nozzle Flange Bolting Material

UG-84(b)(2) was not considered.

UCS-66(g) was not considered.

UCS-66(i) was not considered.

Notes:

Impact test temps were not entered in and not considered in the analysis.

UCS-66(i) applies to impact tested materials not by specification and

UCS-66(g) applies to materials impact tested per UG-84.1 General Note (c).

The Basic MDMT includes the (30F) PWHT credit if applicable.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Class From To : Basic Element Checks.

==========================================================================

Class From To: Check of Additional Element Data

==========================================================================

Warning: CH. Flange and SH. Flange

There are mating flanges in this model that have different design pressures. This

will generate different bolt loads. If a tubesheet is in between these flanges, PV Elite

will compute the mating flange loads for you.  If there is not a tubesheet physically

separating these flanges, you must enter in the mating flange loads into the flange dialog.

Warning:

There is a flange in this model connected to an element whose temperature is different.

The bolt allowable stress is based on it's parent design temperature. You may need to

manually adjust the operating bolt allowable stress to a value based upon a representative

maximum temperature the bolts will be subject to.

Note:

PV Elite performs all calculations internally in Imperial Units

to remain compliant with the ASME Code and any built in assumptions

in the ASME Code formulas. The finalized results are reflected to show

the set of selected units for this analysis.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

PV Elite Vessel Analysis Program: Input Data

Exchanger Design Pressures and Temperatures

Shell Side Design Pressure                                22  bars

Channel Side Design Pressure                             6.8  bars

Shell Side Design Temperature                          120.0  °C

Channel Side Design Temperature                         85.0  °C

Radiography, Shell Side                                 RT-1

Radiography, Channel Side                               RT-1

Service Type, Shell Side                                None

Service Type, Channel Side                              None

MDMT (CET), Shell Side                                 -45.0  °C

MDMT (CET), Tube Side                                  -29.0  °C

User defined MAWP, Shell Side                              0  bars

User defined MAWP, Channel Side                            0  bars

User defined MAPnc, Shell Side                             0  bars

User defined MAPnc, Channel Side                           0  bars

User defined Test Pres., Shell Side                        0  bars

User defined Test Pres., Channel Side                      0  bars

------------------------------------------------------------------

Projection of Nozzle from Vessel Top                       0  mm.

Projection of Nozzle from Vessel Bottom                    0  mm.

Type of Construction                                  Welded

Use Higher Longitudinal Stresses (Flag)                    Y

Select t for Internal Pressure (Flag)                      N

Select t for External Pressure (Flag)                      N

Select t for Axial Stress (Flag)                           N

Select Location for Stiff. Rings (Flag)                    N

Consider Vortex Shedding                                   N

Perform a Corroded Hydrotest                               Y

Shop Pressure Test:

Type of Pressure Test                     UG-99(b) Note [35]

Pressure Test Position                            Horizontal

Load Case 1                                   NP+EW+WI+FW+BW

Load Case 2                                   NP+EW+EE+FS+BS

Load Case 3                                   NP+OW+WI+FW+BW

Load Case 4                                   NP+OW+EQ+FS+BS

Load Case 5                                         NP+HW+HI

Load Case 6                                         NP+HW+HE

Load Case 7                                   IP+OW+WI+FW+BW

Load Case 8                                   IP+OW+EQ+FS+BS

Load Case 9                                   EP+OW+WI+FW+BW

Load Case 10                                  EP+OW+EQ+FS+BS

Load Case 11                                        HP+HW+HI

Load Case 12                                        HP+HW+HE

Load Case 13                                        IP+WE+EW

Load Case 14                                        IP+WF+CW

Load Case 15                                        IP+VO+OW

Load Case 16                                        IP+VE+EW

Load Case 17                                        NP+VO+OW

Load Case 18                                     FS+BS+IP+OW

Load Case 19                                     FS+BS+EP+OW

Wind Design Code                                   UBC-94/97

UBC Design Wind Speed                                    125  Km/hr

UBC Exposure Constant                  D: Flat, unobstructed

UBC Importance Factor                                    1.0

UBC Base Elevation                                     20000  mm.

UBC Percent Wind for Hydrotest                          33.0

Using User defined Wind Press. Vs Elev.                    N

Damping Factor (Beta) for Wind (Ope)                  0.0100

Damping Factor (Beta) for Wind (Empty)                0.0000

Damping Factor (Beta) for Wind (Filled)               0.0000

Seismic Design Code                                 UBC 1997

UBC Seismic Zone (1=1,2=2a,3=2b,4=3,5=4)                   5

UBC Importance Factor                                  1.250

UBC Seismic Coefficient Ca                             0.400

UBC Seismic Coefficient Cv                             0.560

UBC Seismic Coefficient Nv                             1.000

UBC Horizontal Force Factor                            3.000

Apply Allowables per paragraph 1612.3.2                   No

Design Pressure + Static Head                              Y

Consider MAP New and Cold in Noz. Design                   N

Consider External Loads for Nozzle Des.                    Y

Use ASME VIII-1 Appendix 1-9                               N

Material Database Year        Current w/Addenda or Code Year

Configuration Directives:

Do not use Nozzle MDMT Interpretation VIII-1 01-37        No

Use Table G instead of exact equation for "A"            Yes

Shell Head Joints are Tapered                            Yes

Compute "K" in corroded condition                        Yes

Use Code Case 2286                                        No

Use the MAWP to compute the MDMT                         Yes

For thickness ratios <= 0.35, MDMT will be -155F (-104C) Yes

For PWHT & P1 Materials the MDMT can be < -55F (-48C)     No

Using Metric Material Databases, ASME II D                No

Calculate B31.3 type stress for Nozzles with Loads       Yes

Reduce the MDMT due to lower membrane stress             Yes

Consider Longitudinal Stress in MDMT calcs. (Div. 1)     Yes

Complete Listing of Vessel Elements and Details:

Element From Node                                         10

Element To Node                                           20

Element Type                                        Elliptical

Description                                         CH. Head

Distance "FROM" to "TO"                                   50  mm.

Inside Diameter                                          600  mm.

Element Thickness                                         10  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         12  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                 6.8  bars

Design Temperature Internal Pressure                      85  °C

Design External Pressure                                   1  bars

Design Temperature External Pressure                      85  °C

Effective Diameter Multiplier                            1.2

Material Name                                      SA-516 70 [Normalized]

Allowable Stress, Ambient                          137.9  N./mm²

Allowable Stress, Operating                        137.9  N./mm²

Allowable Stress, Hydrotest                        235.8  N./mm²

Material Density                                 0.00775  kg./cm³

P Number Thickness                                30.988  mm.

Yield Stress, Operating                            241.8  N./mm²

UCS-66 Chart Curve Designation                         D

External Pressure Chart Name                        CS-2

UNS Number                                        K02700

Product Form                                       Plate

Efficiency, Longitudinal Seam                            1.0

Efficiency, Circumferential Seam                         1.0

Elliptical Head Factor                                   2.0

Weld is pre-Heated                                        No

Element From Node                                     10

Detail Type                                       Liquid

Detail ID                                     Liquid: 10

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              600  mm.

Liquid Density                                 0.0009181  kg./cm³

Element From Node                                     10

Detail Type                                   Insulation

Detail ID                                        Ins: 10

Dist. from "FROM" Node / Offset dist                -150  mm.

Height/Length of Insulation                          200  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

--------------------------------------------------------------------

Element From Node                                         20

Element To Node                                           30

Element Type                                        Cylinder

Description                                       CH. Barrel

Distance "FROM" to "TO"                                  300  mm.

Inside Diameter                                          600  mm.

Element Thickness                                         10  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         10  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                 6.8  bars

Design Temperature Internal Pressure                      85  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                      85  °C

Effective Diameter Multiplier                            1.2

Material Name                                      SA-516 70 [Normalized]

Efficiency, Longitudinal Seam                            1.0

Efficiency, Circumferential Seam                         1.0

Weld is pre-Heated                                        No

Element From Node                                     20

Detail Type                                       Liquid

Detail ID                                     Liquid: 20

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              600  mm.

Liquid Density                                 0.0009181  kg./cm³

Element From Node                                     20

Detail Type                                   Insulation

Detail ID                                        Ins: 20

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                          300  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

Element From Node                                     20

Detail Type                                       Nozzle

Detail ID                                      T1 (3in.)

Dist. from "FROM" Node / Offset dist                 150  mm.

Nozzle Diameter                                        3  in.

Nozzle Schedule                                       80

Nozzle Class                                         150

Layout Angle                                     108.819

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  11.862  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-106 B

Element From Node                                     20

Detail Type                                       Nozzle

Detail ID                                      T2 (3in.)

Dist. from "FROM" Node / Offset dist                 150  mm.

Nozzle Diameter                                        3  in.

Nozzle Schedule                                       80

Nozzle Class                                         150

Layout Angle                                     251.181

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  11.862  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-106 B

Element From Node                                     20

Detail Type                                       Weight

Detail ID                                     PASS PAR.0

Dist. from "FROM" Node / Offset dist                 150  mm.

Miscellaneous Weight                                  70  Kgf

Offset from Element Centerline                         0  mm.

--------------------------------------------------------------------

Element From Node                                         30

Element To Node                                           40

Element Type                                        Flange

Description                                       CH. Flange

Distance "FROM" to "TO"                                   85  mm.

Flange Inside Diameter                                   600  mm.

Element Thickness                                         60  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         90  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                 6.8  bars

Design Temperature Internal Pressure                      85  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                      85  °C

Effective Diameter Multiplier                            1.2

Material Name                                       SA-266 2

Allowable Stress, Ambient                          137.9  N./mm²

Allowable Stress, Operating                        137.9  N./mm²

Allowable Stress, Hydrotest                        223.4  N./mm²

Material Density                                 0.00775  kg./cm³

P Number Thickness                                30.988  mm.

Yield Stress, Operating                            229.2  N./mm²

UCS-66 Chart Curve Designation                         C

External Pressure Chart Name                        CS-2

UNS Number                                        K03506

Product Form                                    Forgings

Perform Flange Stress Calculation (Y/N)                    Y

Weight of Standard Flange                                  0  Kgf

Class of Standard Flange

Grade of Standard Flange

Weld is pre-Heated                                        No

Element From Node                                     30

Detail Type                                       Liquid

Detail ID                                     Liquid: 30

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              600  mm.

Liquid Density                                 0.0009181  kg./cm³

Element From Node                                     30

Detail Type                                   Insulation

Detail ID                                        Ins: 30

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                           85  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

--------------------------------------------------------------------

Element From Node                                         40

Element To Node                                           50

Element Type                                        Flange

Description                                       SH. Flange

Distance "FROM" to "TO"                                   85  mm.

Flange Inside Diameter                                   600  mm.

Element Thickness                                         60  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         90  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                  22  bars

Design Temperature Internal Pressure                     120  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                     120  °C

Effective Diameter Multiplier                            1.2

Material Name                                     SA-350 LF2 [Impact Tested]

Allowable Stress, Ambient                          137.9  N./mm²

Allowable Stress, Operating                        137.9  N./mm²

Allowable Stress, Hydrotest                        223.4  N./mm²

Material Density                                 0.00775  kg./cm³

P Number Thickness                                30.988  mm.

Yield Stress, Operating                            223.6  N./mm²

UCS-66 Chart Curve Designation             Impact Tested

External Pressure Chart Name                        CS-2

UNS Number                                        K03011

Class / Thickness / Grade                            1::

Product Form                                    Forgings

Perform Flange Stress Calculation (Y/N)                    Y

Weight of Standard Flange                                  0  Kgf

Class of Standard Flange

Grade of Standard Flange

Weld is pre-Heated                                        No

Element From Node                                     40

Detail Type                                       Liquid

Detail ID                                     Liquid: 40

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              600  mm.

Liquid Density                                 0.0005329  kg./cm³

Element From Node                                     40

Detail Type                                   Insulation

Detail ID                                        Ins: 40

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                           85  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

--------------------------------------------------------------------

Element From Node                                         50

Element To Node                                           60

Element Type                                        Cylinder

Description                                      Port Barrel

Distance "FROM" to "TO"                                  150  mm.

Inside Diameter                                          600  mm.

Element Thickness                                         12  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         12  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                  22  bars

Design Temperature Internal Pressure                     120  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                     120  °C

Effective Diameter Multiplier                            1.2

Material Name                                      SA-516 70 [Normalized]

Allowable Stress, Ambient                          137.9  N./mm²

Allowable Stress, Operating                        137.9  N./mm²

Allowable Stress, Hydrotest                        235.8  N./mm²

Material Density                                 0.00775  kg./cm³

P Number Thickness                                30.988  mm.

Yield Stress, Operating                              236  N./mm²

UCS-66 Chart Curve Designation                         D

External Pressure Chart Name                        CS-2

UNS Number                                        K02700

Product Form                                       Plate

Efficiency, Longitudinal Seam                            1.0

Efficiency, Circumferential Seam                         1.0

Weld is pre-Heated                                        No

Element From Node                                     50

Detail Type                                       Liquid

Detail ID                                     Liquid: 50

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              600  mm.

Liquid Density                                 0.0005329  kg./cm³

Element From Node                                     50

Detail Type                                   Insulation

Detail ID                                        Ins: 50

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                          150  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

--------------------------------------------------------------------

Element From Node                                         60

Element To Node                                           70

Element Type                                        Conical

Description                                         SH. Cone

Distance "FROM" to "TO"                                  565  mm.

Inside Diameter                                          600  mm.

Element Thickness                                         12  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         12  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                  22  bars

Design Temperature Internal Pressure                     120  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                     120  °C

Effective Diameter Multiplier                            1.2

Material Name                                      SA-516 70 [Normalized]

Efficiency, Longitudinal Seam                            1.0

Efficiency, Circumferential Seam                         1.0

Cone Diameter at "To" End                                925  mm.

Design Length of Cone                                    565  mm.

Half Apex Angle of Cone                                 30.0  degrees

Toriconical (Y/N)                                          N

Weld is pre-Heated                                        No

Element From Node                                     60

Detail Type                                       Liquid

Detail ID                                     Liquid: 60

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              925  mm.

Liquid Density                                 0.0005329  kg./cm³

Element From Node                                     60

Detail Type                                   Insulation

Detail ID                                        Ins: 60

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                          565  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

Element From Node                                     60

Detail Type                                       Nozzle

Detail ID                                      S1 (4in.)

Dist. from "FROM" Node / Offset dist                 150  mm.

Nozzle Diameter                                        4  in.

Nozzle Schedule                                      120

Nozzle Class                                         300

Layout Angle                                       270.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  25.056  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-333 6 [Impact Tested]

--------------------------------------------------------------------

Element From Node                                         70

Element To Node                                           80

Element Type                                        Cylinder

Description                                       SH. Barrel

Distance "FROM" to "TO"                                 2200  mm.

Inside Diameter                                          925  mm.

Element Thickness                                         12  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         12  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                  22  bars

Design Temperature Internal Pressure                     120  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                     120  °C

Effective Diameter Multiplier                            1.2

Material Name                                      SA-516 70 [Normalized]

Efficiency, Longitudinal Seam                            1.0

Efficiency, Circumferential Seam                         1.0

Weld is pre-Heated                                        No

Element From Node                                     70

Detail Type                                       Saddle

Detail ID                                    Left Saddle

Dist. from "FROM" Node / Offset dist                 230  mm.

Width of Saddle                                      140  mm.

Height of Saddle at Bottom                           750  mm.

Saddle Contact Angle                               120.0

Height of Composite Ring Stiffener                     0  mm.

Width of Wear Plate                                  300  mm.

Thickness of Wear Plate                               12  mm.

Contact Angle, Wear Plate (degrees)                132.0

Friction coefficient                          0.30000001

Moment Factor                                        3.0

Dimension E at base (optional)                         0  mm.

Circumferential Eff. over Saddle                     1.0

Circumferential Eff. at Midspan                      1.0

Tangent to Tangent dist. (optional)                    0  mm.

Element From Node                                     70

Detail Type                                       Saddle

Detail ID                                   Right Saddle

Dist. from "FROM" Node / Offset dist                1650  mm.

Width of Saddle                                      140  mm.

Height of Saddle at Bottom                           750  mm.

Saddle Contact Angle                               120.0

Height of Composite Ring Stiffener                     0  mm.

Width of Wear Plate                                  300  mm.

Thickness of Wear Plate                               12  mm.

Contact Angle, Wear Plate (degrees)                132.0

Friction coefficient                          0.30000001

Moment Factor                                        3.0

Dimension E at base (optional)                         0  mm.

Circumferential Eff. over Saddle                     1.0

Circumferential Eff. at Midspan                      1.0

Tangent to Tangent dist. (optional)                    0  mm.

Element From Node                                     70

Detail Type                                       Liquid

Detail ID                                     Liquid: 70

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              925  mm.

Liquid Density                                 0.0005329  kg./cm³

Element From Node                                     70

Detail Type                                   Insulation

Detail ID                                        Ins: 70

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                         2200  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

Element From Node                                     70

Detail Type                                       Nozzle

Detail ID                                      S2 (6in.)

Dist. from "FROM" Node / Offset dist                1100  mm.

Nozzle Diameter                                        6  in.

Nozzle Schedule                                       80

Nozzle Class                                         300

Layout Angle                                        90.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  47.688  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-333 6 [Impact Tested]

Element From Node                                     70

Detail Type                                       Nozzle

Detail ID                                       V (2in.)

Dist. from "FROM" Node / Offset dist                2050  mm.

Nozzle Diameter                                        2  in.

Nozzle Schedule                                     None

Nozzle Class                                         300

Layout Angle                                        90.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  9.9881  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                   SA-350 LF2 [Impact Tested]

Element From Node                                     70

Detail Type                                       Nozzle

Detail ID                                       D (2in.)

Dist. from "FROM" Node / Offset dist                2050  mm.

Nozzle Diameter                                        2  in.

Nozzle Schedule                                     None

Nozzle Class                                         300

Layout Angle                                       270.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  9.9881  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                   SA-350 LF2 [Impact Tested]

Element From Node                                     70

Detail Type                                       Nozzle

Detail ID                                     PSV (3in.)

Dist. from "FROM" Node / Offset dist                 170  mm.

Nozzle Diameter                                        3  in.

Nozzle Schedule                                      160

Nozzle Class                                         300

Layout Angle                                        90.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  16.474  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-333 6 [Impact Tested]

Element From Node                                     70

Detail Type                                       Nozzle

Detail ID                                     LG1 (2in.)

Dist. from "FROM" Node / Offset dist                 600  mm.

Nozzle Diameter                                        2  in.

Nozzle Schedule                                      160

Nozzle Class                                         300

Layout Angle                                        90.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  6.0973  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-333 6 [Impact Tested]

Element From Node                                     70

Detail Type                                       Nozzle

Detail ID                                     LG2 (2in.)

Dist. from "FROM" Node / Offset dist                 600  mm.

Nozzle Diameter                                        2  in.

Nozzle Schedule                                      160

Nozzle Class                                         300

Layout Angle                                       270.0

Blind Flange (Y/N)                                     N

Weight of Nozzle ( Used if > 0 )                  8.7691  Kgf

Grade of Attached Flange                          GR 1.1

Nozzle Matl                                     SA-333 6 [Impact Tested]

Element From Node                                     70

Detail Type                                       Weight

Detail ID                                  BUNDLE MISS.0

Dist. from "FROM" Node / Offset dist                 100  mm.

Miscellaneous Weight                                 100  Kgf

Offset from Element Centerline                       160  mm.

Element From Node                                     70

Detail Type                                       Weight

Detail ID                                  BUNDLE MISS.0

Dist. from "FROM" Node / Offset dist                1450  mm.

Miscellaneous Weight                                 100  Kgf

Offset from Element Centerline                       160  mm.

--------------------------------------------------------------------

Element From Node                                         80

Element To Node                                           90

Element Type                                        Elliptical

Description                                         SH. Head

Distance "FROM" to "TO"                                   50  mm.

Inside Diameter                                          925  mm.

Element Thickness                                         12  mm.

Internal Corrosion Allowance                               3  mm.

Nominal Thickness                                         14  mm.

External Corrosion Allowance                               0  mm.

Design Internal Pressure                                  22  bars

Design Temperature Internal Pressure                     120  °C

Design External Pressure                              1.0342  bars

Design Temperature External Pressure                     120  °C

Effective Diameter Multiplier                            1.2

Material Name                                      SA-516 70 [Normalized]

Efficiency, Longitudinal Seam                            1.0

Efficiency, Circumferential Seam                         1.0

Elliptical Head Factor                                   2.0

Weld is pre-Heated                                        No

Element From Node                                     80

Detail Type                                       Liquid

Detail ID                                     Liquid: 80

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Liquid                              925  mm.

Liquid Density                                 0.0005329  kg./cm³

Element From Node                                     80

Detail Type                                   Insulation

Detail ID                                        Ins: 80

Dist. from "FROM" Node / Offset dist                   0  mm.

Height/Length of Insulation                       281.25  mm.

Thickness of Insulation                               60  mm.

Density                                          0.00023  kg./cm³

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

XY Coordinate Calculations:

|    |            |            |             |             |

From     | To |  X (Horiz.)|  Y (Vert.) |  DX (Horiz.)|  DY (Vert.) |

|    |        mm. |        mm. |         mm. |         mm. |

----------------------------------------------------------------------

CH. Head|         50 |        ... |          50 |         ... |

CH. Barrel|        350 |        ... |         300 |         ... |

CH. Flange|        435 |        ... |          85 |         ... |

SH. Flange|    598.525 |        ... |          85 |         ... |

Port Barrel|    748.525 |        ... |         150 |         ... |

SH. Cone|    1313.53 |        ... |         565 |         ... |

SH. Barrel|    3513.53 |        ... |        2200 |         ... |

SH. Head|    3563.53 |        ... |          50 |         ... |

----------------------------------------------------------------------

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Flange Input Data Values                         Description: CH. FLANGE    :

CH. Flange

Description of Flange Geometry (Type)           Integral Weld Neck

Design Pressure                            P            6.85  bars

Design Temperature                                        85  °C

Internal Corrosion Allowance              ci          3.0000  mm.

External Corrosion Allowance              ce          0.0000  mm.

Use Corrosion Allowance in Thickness Calcs.              Yes

Flange Inside Diameter                     B         600.000  mm.

Flange Outside Diameter                    A         760.000  mm.

Flange Thickness                           t         60.0000  mm.

Thickness of Hub at Small End             go         10.0000  mm.

Thickness of Hub at Large End             g1         15.0000  mm.

Length of Hub                              h         25.0000  mm.

Flange Material                                     SA-266 2

Flange Material UNS number                            K03506

Flange Allowable Stress At Temperature   Sfo          137.90  N./mm²

Flange Allowable Stress At Ambient       Sfa          137.90  N./mm²

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature      Sb          172.38  N./mm²

Bolt Allowable Stress At Ambient          Sa          172.38  N./mm²

Diameter of Bolt Circle                    C         705.000  mm.

Nominal Bolt Diameter                      a         22.2250  mm.

Type of Threads                           TEMA Thread Series

Number of Bolts                                           20

Flange Face Outside Diameter             Fod         653.000  mm.

Flange Face Inside Diameter              Fid         600.000  mm.

Flange Facing Sketch                       2, Code Sketch 1b

Gasket Outside Diameter                   Go         650.000  mm.

Gasket Inside Diameter                    Gi         624.000  mm.

Gasket Factor                              m          3.0000

Gasket Design Seating Stress               y           69.00  N./mm²

Column for Gasket Seating                  2, Code Column II

Gasket Thickness                          tg          4.5000  mm.

ASME Code, Section VIII Division 1, 2019

Hub Small End Required Thickness due to Internal Pressure:

= (P*(D/2+Ca))/(S*E-0.6*P) per UG-27 (c)(1)

= (6.85*(600/2+3))/(138*1-0.6*6.85)+Ca

= 4.5106 mm.

Hub Small End Hub MAWP:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138 * 1 * 7 )/(303 + 0.6 * 7 )

= 31.421 bars

Corroded Flange Thickness, tc = T-ci                     57.000  mm.

Corroded Flange ID,      Bcor = B+2*Fcor                606.000  mm.

Corroded Large Hub,     g1Cor = g1-ci                    12.000  mm.

Corroded Small Hub,     g0Cor = go-ci                     7.000  mm.

Code R Dimension,           R = ((C-Bcor)/2)-g1cor       37.500  mm.

Gasket Contact Width,       N = (Go - Gi) / 2            13.000  mm.

Basic Gasket Width,        bo = N / 2                     6.500  mm.

Effective Gasket Width,     b = Cb sqrt(bo)               6.425  mm.

Gasket Reaction Diameter,   G = Go - 2 * b              637.151  mm.

Basic Flange and Bolt Loads:

Hydrostatic End Load due to Pressure [H]:

= 0.785 * G² * Peq

= 0.79 * 637² * 6.85

= 22285.168 Kgf

Contact Load on Gasket Surfaces [Hp]:

= 2 * b * Pi * G * m * P

= 2 * 6.42 * 3.14 * 637 * 3 * 6.85

= 5392.977 Kgf

Hydrostatic End Load at Flange ID [Hd]:

= Pi * Bcor² * P  / 4

= 3.14 * 606² *6.85/4

= 20159.355 Kgf

Pressure Force on Flange Face [Ht]:

= H - Hd

= 22285 - 20159

= 2125.812 Kgf

Operating Bolt Load [Wm1]:

= max( H + Hp + H'p, 0 )

= max( 22285 + 5393 + 0, 0 )

= 27678.143 Kgf

= 88967.883 Kgf, Mating Flange Load Governs

Gasket Seating Bolt Load [Wm2]:

= y * b * Pi * G  + yPart * bPart * lp

= 69*6.42*3.141*637+0*0*0

= 90480.758 Kgf

Required Bolt Area [Am]:

= Maximum of Wm1/Sb, Wm2/Sa

= Maximum of 88968/172, 90481/172

= 51.477 cm²

ASME Maximum Circumferential Spacing between Bolts per App. 2 eq. (3) [Bsmax]:

= 2a + 6t/(m + 0.5)

= 2 * 22.2 + 6 * 57/(3 + 0.5)

= 142.164 mm.

Actual Circumferential Bolt Spacing [Bs]:

= C * sin( pi / n )

= 705 * sin( 3.14/20 )

= 110.286 mm.

ASME Moment Multiplier for Bolt Spacing per App. 2 eq. (7) [Bsc]:

= max( sqrt( Bs/( 2a + t )), 1 )

= max( sqrt( 110/( 2 * 22.2 + 57 )), 1 )

= 1.0426

Bolting Information for TEMA Imperial Thread Series (Non Mandatory):

-------------------------------------------------------------------------

Minimum    Actual     Maximum

-------------------------------------------------------------------------

Bolt Area, cm²                              51.477     54.064

Radial Distance between Hub and Bolts:      31.750     37.500

Radial Distance between Bolts and Edge:     23.812     27.500

Circ. Spacing between the Bolts:            52.400    110.286    142.164

-------------------------------------------------------------------------

Min. Gasket Contact Width (Brownell Young) [Not an ASME Calc] [Nmin]:

= Ab * Sa/( y * Pi * (Go + Gi) )

= 54.1  * 172/(69 * 3.14 *(650 + 624 ) )

= 3.375 mm.

Flange Design Bolt Load, Gasket Seating [W]:

= Sa * ( Am + Ab ) / 2

= 172 *( 51.5 + 54.1 )/2

= 92754.98 Kgf

Gasket Load for the Operating Condition [HG]:

= Wm1 - H

= 88968 - 22285

= 66682.71 Kgf

Moment Arm Calculations:

Distance to Gasket Load Reaction [hg]:

= (C - G ) / 2

= ( 705 - 637 )/2

= 33.9246 mm.

Distance to Face Pressure Reaction [ht]:

= ( R + g1 + hg ) / 2

= ( 37.5 + 12 + 33.9 )/2

= 41.7123 mm.

Distance to End Pressure Reaction [hd]:

= R + ( g1 / 2 )

= 37.5 +( 12/2.0 )

= 43.5000 mm.

Summary of Moments for Internal Pressure: (Kg-m.)

Loading                 Force  |   Distance |  Bolt Corr |         Moment  |

----------------------------------------------------------------------------

End Pressure,   Md      20159. |    43.5000 |     1.0426 |            914. |

Face Pressure,  Mt       2126. |    41.7123 |     1.0426 |             92. |

Gasket Load,    Mg      66683. |    33.9246 |     1.0426 |           2359. |

Gasket Seating, Matm    92755. |    33.9246 |     1.0426 |           3281. |

Total Moment for Operation,      Mop                                 3365. Kg-m.

Total Moment for Gasket seating, Matm                                3281. Kg-m.

Effective Hub Length, ho = sqrt(Bcor*goCor)           65.131  mm.

Hub Ratio,          h/h0 = HL / H0                     0.384

Thickness Ratio,   g1/g0 = (g1Cor/goCor)               1.714

Flange Factors for Integral Flange:

Factor F                                               0.858

Factor V                                               0.302

Factor f                                               1.217

Factors from Figure 2-7.1                     K =      1.254

T =      1.817            U =      9.566

Y =      8.705            Z =      4.491

d = 0.10120E+06 mm.³       e =     0.0132 mm.^-1

Stress Factors                            ALPHA =      1.751

BETA =      2.001        GAMMA =      0.964

DELTA =      1.830        Lamda =      2.794

Longitudinal Hub Stress, Operating [SHo]:

= ( f * Mop / Bcor ) / ( L * g1² )

= (1.22*3365/606)/(2.79*12²)

= 164.79 N./mm²

Longitudinal Hub Stress, Seating [SHa]:

= ( f * Matm / Bcor ) / ( L * g1² )

= (1.22*3281/606)/(2.79*12²)

= 160.65 N./mm²

Radial Flange Stress, Operating [SRo]:

= ( Beta * Mop / Bcor ) / ( L * t² )

= (2*3365/606)/(2.79*57²)

= 12.01 N./mm²

Radial Flange Stress, Seating [SRa]:

= ( Beta * Matm/Bcor ) / ( L * t² )

= (2*3281/606)/(2.79*57²)

= 11.71 N./mm²

Tangential Flange Stress, Operating [STo]:

= ( Y * Mo / (t² * Bcor) ) - Z * SRo

= (8.7*3365/(57²*606))-4.49*12

= 91.99 N./mm²

Tangential Flange Stress, Seating [STa]:

= ( y * Matm / (t² * Bcor) ) - Z * SRa

= (8.7*3281/(57²*606))-4.49*11.7

= 89.68 N./mm²

Average Flange Stress, Operating [SAo]:

= ( SHo + max( SRo, STo ) ) / 2

= (165+max(12,92))/2

= 128.39 N./mm²

Average Flange Stress, Seating [SAa]:

= ( SHa + max( SRa, STa ) ) / 2

= (161+max(11.7,89.7))/2

= 125.16 N./mm²

Bolt Stress, Operating [BSo]:

= Wm1 / Ab

= 88968/54.1

= 161.38 N./mm²

Bolt Stress, Seating [BSa]:

= ( Wm2 / Ab )

= (90481/54.1)

= 164.12 N./mm²

Flange Stress Analysis Results: N./mm²

Operating |            Gasket Seating |

Actual       Allowed |      Actual       Allowed |

-----------------------------------------------------------------------------

Longitudinal Hub           164.79 |      206.85 |      160.65 |      206.85 |

Radial Flange               12.01 |      137.90 |       11.71 |      137.90 |

Tangential Flange           91.99 |      137.90 |       89.68 |      137.90 |

Maximum Average            128.39 |      137.90 |      125.16 |      137.90 |

Bolting                    161.38 |      172.38 |      164.12 |      172.38 |

Minimum Required Flange Thickness [Rigidity]          58.242 mm.

Estimated M.A.W.P. ( Operating )                        14.7 bars

Estimated Finished Weight of Flange at given Thk.       84.1 kg.

Estimated Unfinished Weight of Forging at given Thk    112.6 kg.

Flange Rigidity Based on Required Thickness [ASME]:

Flange Rigidity Index, Seating (rotation check) per APP. 2 [Js]:

= 52.14 * Ma / Bsc * Cnv_fac * V / ( Lambda * Eamb * go2 * ho * Ki )

= 52.14*3310/1.05*9807*0.3/(2.61*202713*72*65.1*0.3)

= 0.956   (should be <= 1)

Flange Rigidity Index Operating (rotation check) per APP. 2 [J]:

= 52.14 * Mo / Bsc * Cnv_fac * V / ( Lambda * Eop * goc2 * ho * Ki )

= 52.14*3395/1.05*9807*0.3/(2.61*199054*72*65.1*0.3)

= 0.999   (should be <= 1)

Flange Rigidity Based on Given Thickness [ASME]:

Flange Rigidity Index, Seating (rotation check) per APP. 2 [Js]:

= 52.14 * Ma / Bsc * Cnv_fac * V / ( Lambda * Eamb * go2 * ho * Ki )

= 52.14*3281/1.04*9807*0.3/(2.79*202713*72*65.1*0.3)

= 0.895   (should be <= 1)

Flange Rigidity Index Operating (rotation check) per APP. 2 [J]:

= 52.14 * Mo / Bsc * Cnv_fac * V / ( Lambda * Eop * goc2 * ho * Ki )

= 52.14*3365/1.04*9807*0.3/(2.79*199054*72*65.1*0.3)

= 0.935   (should be <= 1)

Minimum Design Metal Temperature Results:

Thickness Ratio = 0.47, Temperature Reduction per Fig. UCS 66.1 = 37 °C

Min Metal Temp. w/o impact per UCS-66, Curve C             -44 °C

Min Metal Temp. at Required thickness (UCS 66.1)           -48 °C

Note: UCS-66(b)(-c) was considered in the flange MDMT calculation.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Flange Input Data Values                         Description: SH. FLANGE    :

SH. Flange

Description of Flange Geometry (Type)           Integral Weld Neck

Design Pressure                            P           22.03  bars

Design Temperature                                       120  °C

Internal Corrosion Allowance              ci          3.0000  mm.

External Corrosion Allowance              ce          0.0000  mm.

Use Corrosion Allowance in Thickness Calcs.              Yes

Flange Inside Diameter                     B         600.000  mm.

Flange Outside Diameter                    A         760.000  mm.

Flange Thickness                           t         60.0000  mm.

Thickness of Hub at Small End             go         12.0000  mm.

Thickness of Hub at Large End             g1         18.0000  mm.

Length of Hub                              h         25.0000  mm.

Flange Material                                   SA-350 LF2

Flange Material UNS number                            K03011

Flange Allowable Stress At Temperature   Sfo          137.90  N./mm²

Flange Allowable Stress At Ambient       Sfa          137.90  N./mm²

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature      Sb          172.38  N./mm²

Bolt Allowable Stress At Ambient          Sa          172.38  N./mm²

Diameter of Bolt Circle                    C         705.000  mm.

Nominal Bolt Diameter                      a         22.2250  mm.

Type of Threads                           TEMA Thread Series

Number of Bolts                                           20

Flange Face Outside Diameter             Fod         653.000  mm.

Flange Face Inside Diameter              Fid         600.000  mm.

Flange Facing Sketch                       2, Code Sketch 1b

Gasket Outside Diameter                   Go         650.000  mm.

Gasket Inside Diameter                    Gi         624.000  mm.

Gasket Factor                              m          3.0000

Gasket Design Seating Stress               y           69.00  N./mm²

Column for Gasket Seating                  2, Code Column II

Gasket Thickness                          tg          4.5000  mm.

ASME Code, Section VIII Division 1, 2019

Hub Small End Required Thickness due to Internal Pressure:

= (P*(D/2+Ca))/(S*E-0.6*P) per UG-27 (c)(1)

= (22*(600/2+3))/(138*1-0.6*22)+Ca

= 7.8880 mm.

Hub Small End Hub MAWP:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138 * 1 * 9 )/(303 + 0.6 * 9 )

= 40.241 bars

Corroded Flange Thickness, tc = T-ci                     57.000  mm.

Corroded Flange ID,      Bcor = B+2*Fcor                606.000  mm.

Corroded Large Hub,     g1Cor = g1-ci                    15.000  mm.

Corroded Small Hub,     g0Cor = go-ci                     9.000  mm.

Code R Dimension,           R = ((C-Bcor)/2)-g1cor       34.500  mm.

Gasket Contact Width,       N = (Go - Gi) / 2            13.000  mm.

Basic Gasket Width,        bo = N / 2                     6.500  mm.

Effective Gasket Width,     b = Cb sqrt(bo)               6.425  mm.

Gasket Reaction Diameter,   G = Go - 2 * b              637.151  mm.

Basic Flange and Bolt Loads:

Hydrostatic End Load due to Pressure [H]:

= 0.785 * G² * Peq

= 0.79 * 637² * 22

= 71632.844 Kgf

Contact Load on Gasket Surfaces [Hp]:

= 2 * b * Pi * G * m * P

= 2 * 6.42 * 3.14 * 637 * 3 * 22

= 17335.039 Kgf

Hydrostatic End Load at Flange ID [Hd]:

= Pi * Bcor² * P  / 4

= 3.14 * 606² *22/4

= 64799.688 Kgf

Pressure Force on Flange Face [Ht]:

= H - Hd

= 71633 - 64800

= 6833.158 Kgf

Operating Bolt Load [Wm1]:

= max( H + Hp + H'p, 0 )

= max( 71633 + 17335 + 0, 0 )

= 88967.883 Kgf

Gasket Seating Bolt Load [Wm2]:

= y * b * Pi * G  + yPart * bPart * lp

= 69*6.42*3.141*637+0*0*0

= 90480.758 Kgf

Required Bolt Area [Am]:

= Maximum of Wm1/Sb, Wm2/Sa

= Maximum of 88968/172, 90481/172

= 51.477 cm²

ASME Maximum Circumferential Spacing between Bolts per App. 2 eq. (3) [Bsmax]:

= 2a + 6t/(m + 0.5)

= 2 * 22.2 + 6 * 57/(3 + 0.5)

= 142.164 mm.

Actual Circumferential Bolt Spacing [Bs]:

= C * sin( pi / n )

= 705 * sin( 3.14/20 )

= 110.286 mm.

ASME Moment Multiplier for Bolt Spacing per App. 2 eq. (7) [Bsc]:

= max( sqrt( Bs/( 2a + t )), 1 )

= max( sqrt( 110/( 2 * 22.2 + 57 )), 1 )

= 1.0426

Bolting Information for TEMA Imperial Thread Series (Non Mandatory):

-------------------------------------------------------------------------

Minimum    Actual     Maximum

-------------------------------------------------------------------------

Bolt Area, cm²                              51.477     54.064

Radial Distance between Hub and Bolts:      31.750     34.500

Radial Distance between Bolts and Edge:     23.812     27.500

Circ. Spacing between the Bolts:            52.400    110.286    142.164

-------------------------------------------------------------------------

Min. Gasket Contact Width (Brownell Young) [Not an ASME Calc] [Nmin]:

= Ab * Sa/( y * Pi * (Go + Gi) )

= 54.1  * 172/(69 * 3.14 *(650 + 624 ) )

= 3.375 mm.

Flange Design Bolt Load, Gasket Seating [W]:

= Sa * ( Am + Ab ) / 2

= 172 *( 51.5 + 54.1 )/2

= 92754.98 Kgf

Gasket Load for the Operating Condition [HG]:

= Wm1 - H

= 88968 - 71633

= 17335.04 Kgf

Moment Arm Calculations:

Distance to Gasket Load Reaction [hg]:

= (C - G ) / 2

= ( 705 - 637 )/2

= 33.9246 mm.

Distance to Face Pressure Reaction [ht]:

= ( R + g1 + hg ) / 2

= ( 34.5 + 15 + 33.9 )/2

= 41.7123 mm.

Distance to End Pressure Reaction [hd]:

= R + ( g1 / 2 )

= 34.5 +( 15/2.0 )

= 42.0000 mm.

Summary of Moments for Internal Pressure: (Kg-m.)

Loading                 Force  |   Distance |  Bolt Corr |         Moment  |

----------------------------------------------------------------------------

End Pressure,   Md      64800. |    42.0000 |     1.0426 |           2838. |

Face Pressure,  Mt       6833. |    41.7123 |     1.0426 |            297. |

Gasket Load,    Mg      17335. |    33.9246 |     1.0426 |            613. |

Gasket Seating, Matm    92755. |    33.9246 |     1.0426 |           3281. |

Total Moment for Operation,      Mop                                 3748. Kg-m.

Total Moment for Gasket seating, Matm                                3281. Kg-m.

Effective Hub Length, ho = sqrt(Bcor*goCor)           73.851  mm.

Hub Ratio,          h/h0 = HL / H0                     0.339

Thickness Ratio,   g1/g0 = (g1Cor/goCor)               1.667

Flange Factors for Integral Flange:

Factor F                                               0.868

Factor V                                               0.326

Factor f                                               1.295

Factors from Figure 2-7.1                     K =      1.254

T =      1.817            U =      9.566

Y =      8.705            Z =      4.491

d = 0.17564E+06 mm.³       e =     0.0118 mm.^-1

Stress Factors                            ALPHA =      1.670

BETA =      1.893        GAMMA =      0.919

DELTA =      1.054        Lamda =      1.973

Longitudinal Hub Stress, Operating [SHo]:

= ( f * Mop / Bcor ) / ( L * g1² )

= (1.3*3748/606)/(1.97*15²)

= 176.95 N./mm²

Longitudinal Hub Stress, Seating [SHa]:

= ( f * Matm / Bcor ) / ( L * g1² )

= (1.3*3281/606)/(1.97*15²)

= 154.89 N./mm²

Radial Flange Stress, Operating [SRo]:

= ( Beta * Mop / Bcor ) / ( L * t² )

= (1.89*3748/606)/(1.97*57²)

= 17.91 N./mm²

Radial Flange Stress, Seating [SRa]:

= ( Beta * Matm/Bcor ) / ( L * t² )

= (1.89*3281/606)/(1.97*57²)

= 15.68 N./mm²

Tangential Flange Stress, Operating [STo]:

= ( Y * Mo / (t² * Bcor) ) - Z * SRo

= (8.7*3748/(57²*606))-4.49*17.9

= 82.07 N./mm²

Tangential Flange Stress, Seating [STa]:

= ( y * Matm / (t² * Bcor) ) - Z * SRa

= (8.7*3281/(57²*606))-4.49*15.7

= 71.84 N./mm²

Average Flange Stress, Operating [SAo]:

= ( SHo + max( SRo, STo ) ) / 2

= (177+max(17.9,82.1))/2

= 129.51 N./mm²

Average Flange Stress, Seating [SAa]:

= ( SHa + max( SRa, STa ) ) / 2

= (155+max(15.7,71.8))/2

= 113.37 N./mm²

Bolt Stress, Operating [BSo]:

= Wm1 / Ab

= 88968/54.1

= 161.38 N./mm²

Bolt Stress, Seating [BSa]:

= ( Wm2 / Ab )

= (90481/54.1)

= 164.12 N./mm²

Flange Stress Analysis Results: N./mm²

Operating |            Gasket Seating |

Actual       Allowed |      Actual       Allowed |

-----------------------------------------------------------------------------

Longitudinal Hub           176.95 |      206.85 |      154.89 |      206.85 |

Radial Flange               17.91 |      137.90 |       15.68 |      137.90 |

Tangential Flange           82.07 |      137.90 |       71.84 |      137.90 |

Maximum Average            129.51 |      137.90 |      113.37 |      137.90 |

Bolting                    161.38 |      172.38 |      164.12 |      172.38 |

Minimum Required Flange Thickness                     57.937 mm.

Estimated M.A.W.P. ( Operating )                        23.5 bars

Estimated Finished Weight of Flange at given Thk.       85.1 kg.

Estimated Unfinished Weight of Forging at given Thk    112.6 kg.

Flange Rigidity Based on Required Thickness [ASME]:

Flange Rigidity Index, Seating (rotation check) per APP. 2 [Js]:

= 52.14 * Ma / Bsc * Cnv_fac * V / ( Lambda * Eamb * go2 * ho * Ki )

= 52.14*3315/1.05*9807*0.33/(1.85*202713*92*73.9*0.3)

= 0.779   (should be <= 1)

Flange Rigidity Index Operating (rotation check) per APP. 2 [J]:

= 52.14 * Mo / Bsc * Cnv_fac * V / ( Lambda * Eop * goc2 * ho * Ki )

= 52.14*3787/1.05*9807*0.33/(1.85*196922*92*73.9*0.3)

= 0.916   (should be <= 1)

Flange Rigidity Based on Given Thickness [ASME]:

Flange Rigidity Index, Seating (rotation check) per APP. 2 [Js]:

= 52.14 * Ma / Bsc * Cnv_fac * V / ( Lambda * Eamb * go2 * ho * Ki )

= 52.14*3281/1.04*9807*0.33/(1.97*202713*92*73.9*0.3)

= 0.730   (should be <= 1)

Flange Rigidity Index Operating (rotation check) per APP. 2 [J]:

= 52.14 * Mo / Bsc * Cnv_fac * V / ( Lambda * Eop * goc2 * ho * Ki )

= 52.14*3748/1.04*9807*0.33/(1.97*196922*92*73.9*0.3)

= 0.858   (should be <= 1)

Minimum Design Metal Temperature Results:

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Note: UCS-66(b)(-c) was considered in the flange MDMT calculation.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Internal Pressure Results Summary:

Element Thickness, Pressure, Diameter and Allowable Stress :

|    | Int. Press |    Nominal | Total Corr |    Element |  Allowable |

From      | To | + Liq. Hd  |  Thickness |  Allowance |   Diameter |  Stress(SE)|

|    |       bars |        mm. |        mm. |        mm. |     N./mm² |

----------------------------------------------------------------------------------

CH. Head|     6.8543 |         12 |          3 |        600 |      137.9 |

CH. Barrel|     6.8543 |         10 |          3 |        600 |      137.9 |

CH. Flange|      6.854 |         90 |          3 |        600 |      137.9 |

SH. Flange|     22.031 |         90 |          3 |        600 |      137.9 |

Port Barrel|     22.032 |         12 |          3 |        600 |      137.9 |

SH. Cone|     22.048 |         12 |          3 |        925 |      137.9 |

SH. Barrel|     22.048 |         12 |          3 |        925 |      137.9 |

SH. Head|     22.048 |         14 |          3 |        925 |      137.9 |

----------------------------------------------------------------------------------

Element Required Thickness and MAWP :

|    |     Design |   M.A.W.P. |     M.A.P. |    Minimum |   Required |

From      | To |   Pressure |   Corroded | New & Cold |  Thickness |  Thickness |

|    |       bars |       bars |       bars |        mm. |        mm. |

----------------------------------------------------------------------------------

CH. Head|        6.8 |       32.1 |       45.8 |         10 |        4.5 |

CH. Barrel|        6.8 |       31.4 |       45.1 |         10 |    4.51065 |

CH. Flange|        6.8 |       14.6 |       23.5 |         60 |    58.2422 |

SH. Flange|         22 |       23.4 |       23.5 |         60 |    57.9374 |

Port Barrel|         22 |       40.2 |       53.9 |         12 |      7.888 |

SH. Cone|         22 |       22.8 |       30.6 |         12 |    11.6866 |

SH. Barrel|         22 |       26.3 |       35.2 |         12 |    10.5153 |

SH. Head|         22 |       26.8 |       35.7 |         12 |    10.3917 |

----------------------------------------------------------------------------------

Summary of Heat Exchanger Maximum Allowable Working Pressures :

Note:

For Exchanger designs, the following values include MAWPs that

consider the tubesheet, tubes, tube/tubesheet joint etc.  These

values were determined by iteration. Review the tubesheet analysis

report for more information.

Shell Side MAWP     =             22.8 bars

Shell Side MAPnc    =             23.5 bars

Channel Side  MAWP  =             14.6 bars

Channel Side  MAPnc =             19.6 bars

Elements Suitable for Design Internal Pressure.

Internal Pressure Calculation Results:

ASME Code, Section VIII Division 1, 2019

Elliptical Head From 10 To 20 SA-516 70 , UCS-66 Crv. D at 85 °C

CH. Head

Material UNS Number:    K02700

Required Thickness due to Internal Pressure [tr]:

= (P*D*Kcor)/(2*S*E-0.2*P) Appendix 1-4(c)

= (6.85*606*0.99)/(2*138*1-0.2*6.85)

= 1.4873 + 3.0000 = 4.4873 mm.

Note: The thickness required was less than the Code Minimum, therefore

the Code Minimum value of 1.5000 mm. per UG-16 will be used.

Max. Allowable Working Pressure at given Thickness, corroded [MAWP]:

Less Operating Hydrostatic Head Pressure of 0.054 bars

= (2*S*E*t)/(Kcor*D+0.2*t) per Appendix 1-4 (c)

= (2*138*1*7)/(0.99*606+0.2*7)

= 32.2 - 0.054 = 32.1  bars

Maximum Allowable Pressure, New and Cold [MAPNC]:

= (2*S*E*t)/(K*D+0.2*t) per Appendix 1-4 (c)

= (2*138*1*10)/(1*600+0.2*10)

= 45.8 bars

Actual stress at given pressure and thickness, corroded [Sact]:

= (P*(Kcor*D+0.2*t))/(2*E*t)

= (6.85*(0.99*606+0.2*7))/(2*1*7)

= 29.354 N./mm²

Straight Flange Required Thickness:

= (P*R)/(S*E-0.6*P) + c    per UG-27 (c)(1)

= (6.85*303)/(138*1-0.6*6.85)+3

= 4.511 mm.

Straight Flange Maximum Allowable Working Pressure:

Less Operating Hydrostatic Head Pressure of 0.054 bars

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138 * 1 * 9 )/(303 + 0.6 * 9 )

= 40.2 - 0.054 = 40.2  bars

Factor K, corroded condition [Kcor]:

= ( 2 + ( Inside Diameter/( 2 * Inside Head Depth ))2)/6

= ( 2 +( 606/( 2 * 153 ))2)/6

= 0.986992

Percent Elong. per UCS-79, VIII-1-01-57 (75*tnom/Rf)*(1-Rf/Ro)  8.333 %

Note: Please Check Requirements of UCS-79 as Elongation is > 5%.

MDMT Calculations in the Knuckle Portion:

Govrn. thk, tg = 10, tr = 3.18, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.45, Temp. Reduction = 39 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

MDMT Calculations in the Head Straight Flange:

Govrn. thk, tg = 12, tr = 3.24, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.36, Temp. Reduction = 71 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Cylindrical Shell From 20 To 30 SA-516 70 , UCS-66 Crv. D at 85 °C

CH. Barrel

Material UNS Number:    K02700

Required Thickness due to Internal Pressure [tr]:

= (P*R)/(S*E-0.6*P) per UG-27 (c)(1)

= (6.85*303)/(138*1-0.6*6.85)

= 1.5106 + 3.0000 = 4.5106 mm.

Max. Allowable Working Pressure at given Thickness, corroded [MAWP]:

Less Operating Hydrostatic Head Pressure of 0.054 bars

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138*1*7)/(303+0.6*7)

= 31.4 - 0.054 = 31.4  bars

Maximum Allowable Pressure, New and Cold [MAPNC]:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138*1*10)/(300+0.6*10)

= 45.1 bars

Actual stress at given pressure and thickness, corroded [Sact]:

= (P*(R+0.6*t))/(E*t)

= (6.85*(303+0.6*7))/(1*7)

= 30.082 N./mm²

% Elongation per Table UG-79-1 (50*tnom/Rf*(1-Rf/Ro))  1.639 %

Minimum Design Metal Temperature Results:

Govrn. thk, tg = 10, tr = 3.24, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.46, Temp. Reduction = 38 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Cylindrical Shell From 50 To 60 SA-516 70 , UCS-66 Crv. D at 120 °C

Port Barrel

Material UNS Number:    K02700

Required Thickness due to Internal Pressure [tr]:

= (P*R)/(S*E-0.6*P) per UG-27 (c)(1)

= (22*303)/(138*1-0.6*22)

= 4.8880 + 3.0000 = 7.8880 mm.

Max. Allowable Working Pressure at given Thickness, corroded [MAWP]:

Less Operating Hydrostatic Head Pressure of 0.032 bars

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138*1*9)/(303+0.6*9)

= 40.2 - 0.032 = 40.2  bars

Maximum Allowable Pressure, New and Cold [MAPNC]:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138*1*12)/(300+0.6*12)

= 53.9 bars

Actual stress at given pressure and thickness, corroded [Sact]:

= (P*(R+0.6*t))/(E*t)

= (22*(303+0.6*9))/(1*9)

= 75.499 N./mm²

% Elongation per Table UG-79-1 (50*tnom/Rf*(1-Rf/Ro))  1.961 %

Minimum Design Metal Temperature Results:

Govrn. thk, tg = 12, tr = 5.06, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.56, Temp. Reduction = 26 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Conical Section From 60 To 70 SA-516 70 , UCS-66 Crv. D at 120 °C

SH. Cone

Material UNS Number:    K02700

Required Thickness due to Internal Pressure [tr]:

= (P*D)/(2*cos(a)*(S*E-0.6*P)) per Appendix 1-4 (e)

= (22*932)/(2*0.87*(138*1-0.6*22))

= 8.6866 + 3.0000 = 11.6866 mm.

Max. Allowable Working Pressure at given Thickness, corroded [MAWP]:

Less Operating Hydrostatic Head Pressure of 0.048 bars

= (2*S*E*t*cos(a))/(D+1.2*t*cos(a)) per App 1-4(e)

= (2*138*1*9*0.87)/(932+1.2*9*0.87)

= 22.8 - 0.048 = 22.8  bars

Maximum Allowable Pressure, New and Cold [MAPNC]:

= (2*S*E*t*cos(a))/(D+1.2*t*cos(a)) per App 1-4(e)

= (2*138*1*12*0.87)/(925+1.2*12*0.87)

= 30.6 bars

Actual stress at given pressure and thickness, corroded [Sact]:

= (P*(D+1.2*t*cos(a)))/(2*E*t*cos(a))

= (22*(932+1.2*9*0.87))/(2*1*9*0.87)

= 133.144 N./mm²

% Elongation per Table UG-79-1 (50*tnom/Rf*(1-Rf/Ro))  1.955 %

Minimum Design Metal Temperature Results:

Govrn. thk, tg = 12, tr = 8.98, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 1, Temp. Reduction = 0 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Cylindrical Shell From 70 To 80 SA-516 70 , UCS-66 Crv. D at 120 °C

SH. Barrel

Material UNS Number:    K02700

Required Thickness due to Internal Pressure [tr]:

= (P*R)/(S*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.5153 + 3.0000 = 10.5153 mm.

Max. Allowable Working Pressure at given Thickness, corroded [MAWP]:

Less Operating Hydrostatic Head Pressure of 0.048 bars

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138*1*9)/(466+0.6*9)

= 26.4 - 0.048 = 26.3  bars

Maximum Allowable Pressure, New and Cold [MAPNC]:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138*1*12)/(462+0.6*12)

= 35.2 bars

Actual stress at given pressure and thickness, corroded [Sact]:

= (P*(R+0.6*t))/(E*t)

= (22*(466+0.6*9))/(1*9)

= 115.369 N./mm²

% Elongation per Table UG-79-1 (50*tnom/Rf*(1-Rf/Ro))  1.281 %

Minimum Design Metal Temperature Results:

Govrn. thk, tg = 12, tr = 7.77, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.86, Temp. Reduction = 8 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Elliptical Head From 80 To 90 SA-516 70 , UCS-66 Crv. D at 120 °C

SH. Head

Material UNS Number:    K02700

Required Thickness due to Internal Pressure [tr]:

= (P*D*Kcor)/(2*S*E-0.2*P) Appendix 1-4(c)

= (22*931*0.99)/(2*138*1-0.2*22)

= 7.3917 + 3.0000 = 10.3917 mm.

Max. Allowable Working Pressure at given Thickness, corroded [MAWP]:

Less Operating Hydrostatic Head Pressure of 0.048 bars

= (2*S*E*t)/(Kcor*D+0.2*t) per Appendix 1-4 (c)

= (2*138*1*9)/(0.99*931+0.2*9)

= 26.8 - 0.048 = 26.8  bars

Maximum Allowable Pressure, New and Cold [MAPNC]:

= (2*S*E*t)/(K*D+0.2*t) per Appendix 1-4 (c)

= (2*138*1*12)/(1*925+0.2*12)

= 35.7 bars

Actual stress at given pressure and thickness, corroded [Sact]:

= (P*(Kcor*D+0.2*t))/(2*E*t)

= (22*(0.99*931+0.2*9))/(2*1*9)

= 113.296 N./mm²

Straight Flange Required Thickness:

= (P*R)/(S*E-0.6*P) + c    per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)+3

= 10.515 mm.

Straight Flange Maximum Allowable Working Pressure:

Less Operating Hydrostatic Head Pressure of 0.048 bars

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (138 * 1 * 11 )/(466 + 0.6 * 11 )

= 32.1 - 0.048 = 32.1  bars

Factor K, corroded condition [Kcor]:

= ( 2 + ( Inside Diameter/( 2 * Inside Head Depth ))2)/6

= ( 2 +( 931/( 2 * 234 ))2)/6

= 0.991489

Percent Elong. per UCS-79, VIII-1-01-57 (75*tnom/Rf)*(1-Rf/Ro)  6.393 %

Note: Please Check Requirements of UCS-79 as Elongation is > 5%.

MDMT Calculations in the Knuckle Portion:

Govrn. thk, tg = 12, tr = 7.64, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.85, Temp. Reduction = 8 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

MDMT Calculations in the Head Straight Flange:

Govrn. thk, tg = 14, tr = 7.77, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.71, Temp. Reduction = 16 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Note: Heads and Shells Exempted to -20F (-29C) by paragraph UG-20F

Hydrostatic Test Pressure Results:

Exchanger Shell Side Hydrostatic Test Pressures:

Pressure per UG99b     = 1.30 * M.A.W.P. * Sa/S         29.624  bars

Pressure per UG99b[35] = 1.30 * Design Pres * Sa/S      28.600  bars

Pressure per UG99c     = 1.30 * M.A.P. - Head(Hyd)      30.501  bars

Pressure per UG100     = 1.10 * M.A.W.P. * Sa/S         25.066  bars

Pressure per PED       = max(1.43*DP, 1.25*DP*ratio)    31.460  bars

Pressure per App 27-4  = M.A.W.P.                       22.788  bars

Exchanger Channel Side Hydrostatic Test Pressures:

Pressure per UG99b     = 1.30 * M.A.W.P. * Sa/S         19.018  bars

Pressure per UG99b[35] = 1.30 * Design Pres * Sa/S       8.840  bars

Pressure per UG99c     = 1.30 * M.A.P. - Head(Hyd)      25.480  bars

Pressure per UG100     = 1.10 * M.A.W.P. * Sa/S         16.092  bars

Pressure per PED       = max(1.43*DP, 1.25*DP*ratio)     9.724  bars

Pressure per App 27-4  = M.A.W.P.                       14.629  bars

UG-99(b) Note 35, Test Pressure Calculation [Shell Side]:

= Test Factor * Design Pressure * Stress Ratio

= 1.3 * 22 * 1

= 28.600 bars

UG-99(b) Note 35, Test Pressure Calculation [Channel Side]:

= Test Factor * Design Pressure * Stress Ratio

= 1.3 * 6.8 * 1

= 8.840 bars

Horizontal Test performed per: UG-99b (Note 35)

Please note that Nozzle, Shell, Head, Flange, etc MAWPs are all considered

when determining the hydrotest pressure for those test types that are based

on the MAWP of the vessel.

Stresses on Elements due to Test Pressure (N./mm² & bars):

From To              |    Stress |  Allowable |       Ratio | Pressure |

------------------------------------------------------------------------

CH. Head             |      38.1 |      235.8 |       0.162 |     8.90 |

CH. Barrel           |      39.1 |      235.8 |       0.166 |     8.90 |

Port Barrel          |      98.2 |      235.8 |       0.416 |    28.66 |

SH. Cone             |     173.3 |      235.8 |       0.735 |    28.69 |

SH. Barrel           |     150.1 |      235.8 |       0.637 |    28.69 |

SH. Head             |     147.4 |      235.8 |       0.625 |    28.69 |

------------------------------------------------------------------------

Stress ratios for Nozzle and Pad Materials (N./mm²):

Description          | Pad/Nozzle |   Ambient |    Operating |   Ratio |

------------------------------------------------------------------------

T1 (3in.)            |     Nozzle |    117.90 |       117.90 |   1.000 |

T1 (3in.)            |        Pad |    137.90 |       137.90 |   1.000 |

T2 (3in.)            |     Nozzle |    117.90 |       117.90 |   1.000 |

T2 (3in.)            |        Pad |    137.90 |       137.90 |   1.000 |

S1 (4in.)            |     Nozzle |    117.90 |       117.90 |   1.000 |

S1 (4in.)            |        Pad |    137.90 |       137.90 |   1.000 |

S2 (6in.)            |     Nozzle |    117.90 |       117.90 |   1.000 |

S2 (6in.)            |        Pad |    137.90 |       137.90 |   1.000 |

V (2in.)             |     Nozzle |    137.90 |       137.90 |   1.000 |

D (2in.)             |     Nozzle |    137.90 |       137.90 |   1.000 |

PSV (3in.)           |     Nozzle |    117.90 |       117.90 |   1.000 |

PSV (3in.)           |        Pad |    137.90 |       137.90 |   1.000 |

LG1 (2in.)           |     Nozzle |    117.90 |       117.90 |   1.000 |

LG2 (2in.)           |     Nozzle |    117.90 |       117.90 |   1.000 |

------------------------------------------------------------------------

Minimum                                                          1.000

Stress ratios for Pressurized Vessel Elements (N./mm²):

Description                       |   Ambient |    Operating |   Ratio |

------------------------------------------------------------------------

CH. Head                          |    137.90 |       137.90 |   1.000 |

CH. Barrel                        |    137.90 |       137.90 |   1.000 |

CH. Flange                        |    137.90 |       137.90 |   1.000 |

SH. Flange                        |    137.90 |       137.90 |   1.000 |

Port Barrel                       |    137.90 |       137.90 |   1.000 |

SH. Cone                          |    137.90 |       137.90 |   1.000 |

SH. Barrel                        |    137.90 |       137.90 |   1.000 |

SH. Head                          |    137.90 |       137.90 |   1.000 |

------------------------------------------------------------------------

Minimum                                                          1.000

Stress ratios for Exchanger Materials (N./mm²):

Description                       |   Ambient |    Operating |   Ratio |

------------------------------------------------------------------------

Tube Material                     |    117.90 |       117.90 |   1.000 |

Tubesheet Material                |    137.90 |       137.90 |   1.000 |

------------------------------------------------------------------------

Minimum                                                          1.000

Hoop Stress in Nozzle Wall during Pressure Test (N./mm²):

Description                       |   Ambient |    Operating |   Ratio |

------------------------------------------------------------------------

T1 (3in.)                         |     10.43 |       217.19 |   0.048 |

T2 (3in.)                         |     10.43 |       217.19 |   0.048 |

S1 (4in.)                         |     23.20 |       217.20 |   0.107 |

S2 (6in.)                         |     35.42 |       217.19 |   0.163 |

V (2in.)                          |      7.71 |       223.40 |   0.035 |

D (2in.)                          |      7.71 |       223.40 |   0.035 |

PSV (3in.)                        |     17.79 |       217.19 |   0.082 |

LG1 (2in.)                        |     17.48 |       217.19 |   0.080 |

LG2 (2in.)                        |     17.48 |       217.19 |   0.080 |

------------------------------------------------------------------------

Elements Suitable for Test Pressure.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

External Pressure Calculation Results :

External Pressure Calculations:

|      |    Section |    Outside |  Corroded |    Factor  |     Factor |

From|   To |     Length |   Diameter | Thickness |       A    |        B   |

|      |        mm. |        mm. |       mm. |            |     N./mm² |

-----------------------------------------------------------------------------

10|    20|    No Calc |        620 |         7 |  0.0015681 |    97.9287 |

20|    30|        400 |        620 |         7 |  0.0026194 |    109.396 |

30|    40|    No Calc |        ... |        57 |    No Calc |    No Calc |

40|    50|    No Calc |        ... |        57 |    No Calc |    No Calc |

50|    60|        150 |        624 |         9 |   0.012325 |    122.731 |

60|    70|    2892.08 |    952.713 |         9 | 0.00030613 |    30.6064 |

70|    80|    2892.08 |        949 |         9 | 0.00038034 |    38.0256 |

80|    90|    No Calc |        949 |         9 |  0.0013172 |     93.319 |

-----------------------------------------------------------------------------

External Pressure Calculations:

|      |   External |   External |        External |    External |

From|   To |  Actual T. | Required T.| Design Pressure |    M.A.W.P. |

|      |        mm. |        mm. |            bars |        bars |

-----------------------------------------------------------------------

10|    20|         10 |    4.57853 |               1 |        12.3 |

20|    30|         10 |    4.65419 |         1.03419 |        16.5 |

30|    40|         60 |     57.277 |         1.03419 |     No Calc |

40|    50|         60 |    53.5432 |         1.03419 |     No Calc |

50|    60|         12 |    4.10182 |         1.03419 |        23.6 |

60|    70|         12 |    8.61227 |         1.03419 |        3.34 |

70|    80|         12 |    7.84861 |         1.03419 |        4.81 |

80|    90|         12 |    5.45716 |         1.03419 |        9.83 |

-----------------------------------------------------------------------

Minimum                                                       3.34

External Pressure Calculations:

|      |   Actual Length | Allowable Length | Ring Inertia | Ring Inertia |

From|   To | Bet. Stiffeners |  Bet. Stiffeners |     Required |    Available |

|      |             mm. |              mm. |        cm**4 |        cm**4 |

--------------------------------------------------------------------------------

10|    20|         No Calc |          No Calc |      No Calc |      No Calc |

20|    30|             400 |            11389 |      No Calc |      No Calc |

30|    40|         No Calc |          No Calc |      No Calc |      No Calc |

40|    50|         No Calc |          No Calc |      No Calc |      No Calc |

50|    60|             150 |          3156.37 |      No Calc |      No Calc |

60|    70|         2892.08 |          2892.08 |      No Calc |      No Calc |

70|    80|         2892.08 |          61083.1 |      No Calc |      No Calc |

80|    90|         No Calc |          No Calc |      No Calc |      No Calc |

--------------------------------------------------------------------------------

Elements Suitable for External Pressure.

ASME Code, Section VIII Division 1, 2019

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Element and Detail Weights:

|    |    Element |    Element |  Corroded |   Corroded | Extra due  |

From| To | Metal Wgt. | ID  Volume |Metal Wgt. |  ID Volume | Misc %     |

|    |        kg. |        Cm. |       kg. |        Cm. |        kg. |

---------------------------------------------------------------------------

10|  20|    50.6331 |    42419.1 |   37.9748 |    43560.2 |    3.03799 |

20|  30|    44.5585 |    84838.2 |   31.3443 |    86543.5 |    2.67351 |

30|  40|    123.873 |    33032.9 |   118.807 |      33175 |    7.43237 |

40|  50|    124.828 |    33032.9 |   119.762 |      33175 |    7.48967 |

50|  60|    26.8228 |    26340.9 |   20.2156 |    27193.6 |    1.60936 |

60|  70|    147.993 |     201391 |    111.49 |     206101 |    8.87957 |

70|  80|    602.315 |    1250746 |   453.181 |    1269991 |    36.1389 |

80|  90|    130.511 |     137226 |   102.544 |     139693 |    7.83066 |

---------------------------------------------------------------------------

Total |       1251 | 1809026.62 |       995 | 1839432.50 |         75 |

For elements specified as shell side elements, the volume(s) shown

above for those elements, reflects the displacement of the tubes.

Weight of Details:

|    |  Weight of |  X Offset, | Y Offset, |    Z Offset |

From|Type|     Detail | Dtl. Cent. |Dtl. Cent. |  Dtl. Cent. | Description

|    |        kg. |        mm. |       mm. |         mm. |

---------------------------------------------------------------

10|Liqd|    38.9339 |        -50 0.18167E-04 |         ... |   Liquid: 10

10|Insl|    10.0491 |        -50 |       ... |         ... |   Ins: 10

20|Liqd|    77.8679 |        150 |       ... |         ... |   Liquid: 20

20|Insl|    8.84351 |        150 |       ... |         ... |   Ins: 20

20|Nozl|    12.5737 |        150 |   326.037 |    -111.113 |   T1 (3in.)

20|Nozl|    12.5737 |        150 |  -326.037 |    -111.113 |   T2 (3in.)

20|Wght|         70 |        150 |       ... |         ... |   PASS PAR.

30|Liqd|    30.3189 |       42.5 |       ... |         ... |   Liquid: 30

30|Insl|    4.60465 |       42.5 |       ... |         ... |   Ins: 30

40|Liqd|    17.5991 |       42.5 |       ... |         ... |   Liquid: 40

40|Insl|    4.64015 |       42.5 |       ... |         ... |   Ins: 40

50|Liqd|    14.0338 |         75 |       ... |         ... |   Liquid: 50

50|Insl|    4.44777 |         75 |       ... |         ... |   Ins: 50

60|Liqd|    107.296 |    217.188 |    -81.25 |         ... |   Liquid: 60

60|Insl|    23.6443 |      282.5 |       ... |         ... |   Ins: 60

60|Nozl|    26.5597 |        150 |   -519.65 |         ... |   S1 (4in.)

70|Sadl|    105.632 |        230 |    594.25 |         ... |   Left Saddle

70|Sadl|    105.632 |       1650 |    594.25 |         ... |   Right Saddle

70|Liqd|    666.365 |       1100 |       ... |         ... |   Liquid: 70

70|Insl|    96.2295 |       1100 |       ... |         ... |   Ins: 70

70|Nozl|    50.5487 |       1100 |   546.637 |         ... |   S2 (6in.)

70|Nozl|    10.5874 |       2050 |     487.9 |         ... |   V (2in.)

70|Nozl|    10.5874 |       2050 |    -487.9 |         ... |   D (2in.)

70|Nozl|    17.4622 |        170 |    506.95 |         ... |   PSV (3in.)

70|Nozl|    6.46311 |        600 |   485.017 |         ... |   LG1 (2in.)

70|Nozl|    9.29522 |        600 |  -485.017 |         ... |   LG2 (2in.)

70|Wght|        100 |        100 |       ... |         160 |   BUNDLE MISS.

70|Wght|        100 |       1450 |       ... |         160 |   BUNDLE MISS.

80|Liqd|    73.1104 |    127.083 |       ... |         ... |   Liquid: 80

80|Insl|    20.8513 |    140.625 |       ... |         ... |   Ins: 80

30|FTsh|    110.743 |        124 |       ... |         ... |   Tubesheet

30|Tube|    781.029 |       1344 |       ... |         ... |   Tubes

---------------------------------------------------------------

Total Weight of Each Detail Type:

Saddles                           211.3

Liquid                           1025.5

Insulation                        173.3

Nozzles                           156.7

Weights                           270.0

Exchanger Components              891.8

Liquid in Tubes                   200.8

-------------------------------------------

Sum of the Detail Weights        2929.4 kg.

Weight Summation Results: (kg.)

| Fabricated |  Shop Test |   Shipping |    Erected |      Empty |  Operating |

---------------------------------------------------------------------------------------------

Main Elements |     1326.6 |     1326.6 |     1326.6 |     1326.6 |     1326.6 |     1326.6 |

Saddles |      211.3 |      211.3 |      211.3 |      211.3 |      211.3 |      211.3 |

Nozzles |      156.7 |      156.7 |      156.7 |      156.7 |      156.7 |      156.7 |

Wld Weights |      270.0 |      270.0 |      270.0 |      270.0 |      270.0 |      270.0 |

Exchanger |      891.8 |      891.8 |      891.8 |      891.8 |      891.8 |      891.8 |

Insulation |        ... |        ... |        ... |      173.3 |      173.3 |      173.3 |

Ope. Liquid |        ... |        ... |        ... |        ... |        ... |     1025.5 |

Tube Ope Lqd |        ... |        ... |        ... |        ... |        ... |      200.8 |

Test Liquid |        ... |     1807.9 |        ... |        ... |        ... |        ... |

Tube Tst Lqd |        ... |      218.7 |        ... |        ... |        ... |        ... |

---------------------------------------------------------------------------------------------

Totals |     2856.3 |     4882.9 |     2856.3 |     3029.6 |     3029.6 |     4256.0 |

Field Installation Options:

Insulation installed before lifting.

Miscellaneous Weight Percent: 6.0 %

Note that the above value for the miscellaneous weight percent has

been applied to the shells/heads/flange/tubesheets/tubes etc. in the

weight calculations for metallic components.

Weight Summary:

Fabricated Wt.  - Bare Weight without Removable Internals                  2856.3 kg.

Shop Test Wt.   - Fabricated Weight + Water ( Full )                       4882.9 kg.

Shipping Wt.    - Fab. Weight + removable Intls.+ Shipping App.            2856.3 kg.

Erected  Wt.    - Fab. Wt + or - loose items (trays,platforms etc.)        3029.6 kg.

Ope. Wt. no Liq - Fab. Weight + Internals. + Details + Weights             3029.6 kg.

Operating Wt.   - Empty Weight + Operating Liq. Uncorroded                 4256.0 kg.

Oper. Wt. + CA  - Corr Wt. + Operating Liquid                              3984.4 kg.

Field Test Wt.  - Empty Weight + Water (Full)                              4815.0 kg.

Exchanger Tube Data

Volume of Exchanger tubes  :                       218814.7 Cm.

Weight of Ope Liq in tubes :                          200.8 kg.

Weight of Water in tubes   :                          218.7 kg.

Note:

The Corroded Weight and thickness are used in the Horizontal

Vessel Analysis (Ope Case) and Earthquake Load Calculations.

Note: The Field Test weight as computed in the corroded condition.

Outside Surface Areas of Elements:

|    |        Surface |

From| To |           Area |

|    |            cm² |

----------------------------

10|  20|        5200.96 |

20|  30|        5843.36 |

30|  40|        4352.68 |

40|  50|        4357.39 |

50|  60|        2940.53 |

60|  70|        14594.9 |

70|  80|        65590.2 |

80|  90|        11341.8 |

----------------------------

Total        114221.789 cm²

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Nozzle Flange MAWP Results: (bars & °C)

Nozzle        |    Flange Rating | Design |       | Grade/ | Equiv. | - - - - - - Max Pressure |

Description   |   Ope. | Ambient |   Temp | Class | Group  |  Press |UG-44(b)|     50% |   DNV |

------------------------------------------------------------------------------------------------

T1 (3in.)     |  18.15 |   19.60 |    85  |   150 | GR 1.1 |    ... |    ... |     ... |   ... |

T2 (3in.)     |  18.15 |   19.60 |    85  |   150 | GR 1.1 |    ... |    ... |     ... |   ... |

S1 (4in.)     |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

S2 (6in.)     |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

V (2in.)      |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

D (2in.)      |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

PSV (3in.)    |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

LG1 (2in.)    |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

LG2 (2in.)    |  46.00 |   51.10 |   120  |   300 | GR 1.1 |    ... |    ... |     ... |   ... |

Shellside Flange Rating

Lowest Flange Pressure Rating was (Ope)[ShellSide]:     46.000  bars

Lowest Flange Pressure Rating was (Amb)[ShellSide]:     51.100  bars

Channelside Flange Rating

Lowest Flange Pressure Rating was (Ope)[TubeSide ]:     18.150  bars

Lowest Flange Pressure Rating was (Amb)[TubeSide ]:     19.600  bars

Pressure Ratings are per ASME B16.5 2013 Metric Edition

Warning:

There are nozzles in this model, but no flange MAWPs were de-rated.  Be

sure this is what you intended.  There is a check box in the nozzle dialog

that instructs PV Elite to perform the de-rating for each nozzle flange.

See ASME VIII-1, UG-44(b) for more information.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Wind Load Calculation Results:

Wind Analysis Results per UBC 1994 or UBC 1997

Importance Factor as Entered by the User is           1.000

Wind Stagnation Pressure (qs) from Table 16-F        75.6     Kgs/m²

Pressure Coefficient from Table 16-H              Cq 0.800

User Entered Basic Wind Speed                         125.0      Km/hr

P(height) = Ce(height,Exp) * Cq * qs * Imp Fact. [18-1](1994) or [20-1](1997)

The values of Ce are shown as the in the table below:

Element                       Ce

--------------------------------

CH. Head                  1.7635

CH. Barrel                1.7635

CH. Flange                1.7635

SH. Flange                1.7635

Port Barrel               1.7635

SH. Cone                  1.7635

SH. Barrel                1.7635

SH. Head                  1.7635

Wind Loads on Masses/Equipment/Piping

ID              Wind Area   Elevation    Pressure       Force

cm²         mm.          Kgs/m²         Kgf

-------------------------------------------------------------------------

PASS PAR.            0.00    20750.00      106.62        0.00

BUNDLE MISS.         0.00    20750.00      106.62        0.00

BUNDLE MISS.         0.00    20750.00      106.62        0.00

Wind Load Calculation:

|    |      Wind  |       Wind |      Wind |      Wind  |    Element |

From| To |    Height  |   Diameter |      Area |  Pressure  |  Wind Load |

|    |        mm. |        mm. |       cm² |     Kgs/m² |        Kgf |

---------------------------------------------------------------------------

10|  20|      20750 |        888 |   1722.63 |    106.618 |    18.3664 |

20|  30|      20750 |        888 |      2664 |    106.618 |    28.4032 |

30|  40|      20750 |        864 |     734.4 |    106.618 |    7.83008 |

40|  50|      20750 |        864 |     734.4 |    106.618 |    7.83008 |

50|  60|      20750 |      892.8 |    1339.2 |    106.618 |    14.2784 |

60|  70|      20750 |     1087.8 |   6146.07 |    106.618 |    65.5286 |

70|  80|      20750 |     1282.8 |   28221.6 |    106.618 |    300.895 |

80|  90|      20750 |     1282.8 |   3187.46 |    106.618 |    33.9843 |

---------------------------------------------------------------------------

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Earthquake Load Calculation Results:

Earthquake Analysis Results  per UBC 1997

The UBC Zone Factor for the Vessel is .............    0.4000

The Importance Factor as Specified by the User is       1.250

The UBC Force Factor as Specified by the User is ..     3.000

The UBC Total Weight (W) for the Vessel is ........    3984.4  Kgf

The UBC Total Shear (V) for the Vessel is .........     976.2  Kgf

The UBC Seismic Coefficient Value Ca is ...........     0.400

The UBC Seismic Coefficient Value Cv is ...........     0.560

The UBC Near Source Factor Nv ( used with zone 4 ).     1.000

Note: The base shear printed above has been modified

by the user defined Earthquake scalar.

Calculation Steps for Computing the design Base Shear (V) per UBC 1997

Computation of V per equation (34-1):

V = 0.7 * Ca * I * W

V = 0.7 * 0.4 * 1.25 * 3984

V = 1394.5 Kgf

Computation of V per equation (30-5):

V = 2.5 * Ca * I * W / R

V = 2.5 * 0.4 * 1.25 * 3984/3

V = 1660.2 Kgf

The computed base shear is the minimum of V from 34-1 and 30-5.

Computation of V per equation (34-2), minimum V.  V cannot be less than

this value !

V = 0.56 * Ca * I * W

V = 0.56 * 0.4 * 1.25 * 3984

V = 1115.6 Kgf

In Zone 4, the Base Shear V may also not be less than the following(34-3):

V = 1.6 * Z * Nv * I * W / R

V = 1.6 * 0.4 * 1 * 1.25 * 3984/3

V = 1062.5 Kgf

Total Adjusted Base Shear V:

= V * Scalar Multiplier = 1394.5 * 0.7000 = 976.2 Kgf

Next Sum the earthquake weights times their heights (wi*hi):

Current Sum = Prev. Sum + Wght 398. * Hght 300.000 = 120.

Current Sum = Prev. Sum + Wght 398. * Hght 300.000 = 239.

Current Sum = Prev. Sum + Wght 398. * Hght 300.000 = 359.

Current Sum = Prev. Sum + Wght 398. * Hght 300.000 = 478.

Current Sum = Prev. Sum + Wght 398. * Hght 300.000 = 598.

Current Sum = Prev. Sum + Wght 398. * Hght 300.000 = 717.

Current Sum = Prev. Sum + Wght 398. * Hght 462.500 = 901.

Current Sum = Prev. Sum + Wght 398. * Hght 462.500 = 1086.

Current Sum = Prev. Sum + Wght 398. * Hght 462.500 = 1270.

Current Sum = Prev. Sum + Wght 398. * Hght 462.500 = 1454.

Compute the load at each level based on equation 30-15 and multiply

by the load case scalar.  The sum will be the total adjusted shear.

Fx = ( V * wx * hx / ( sum of ( wi * hi ))) * EqFact

Fx = [(1395.) * 398. * 300.000 / 1454.]*.7000 = 80.

Fx = [(1395.) * 398. * 300.000 / 1454.]*.7000 = 80.

Fx = [(1395.) * 398. * 300.000 / 1454.]*.7000 = 80.

Fx = [(1395.) * 398. * 300.000 / 1454.]*.7000 = 80.

Fx = [(1395.) * 398. * 300.000 / 1454.]*.7000 = 80.

Fx = [(1395.) * 398. * 300.000 / 1454.]*.7000 = 80.

Fx = [(1395.) * 398. * 462.500 / 1454.]*.7000 = 124.

Fx = [(1395.) * 398. * 462.500 / 1454.]*.7000 = 124.

Fx = [(1395.) * 398. * 462.500 / 1454.]*.7000 = 124.

Fx = [(1395.) * 398. * 462.500 / 1454.]*.7000 = 124.

Earthquake Load Calculation:

|    | Earthquake | Earthquake |   Element |

From| To |     Height |     Weight | Ope  Load |

|    |        mm. |        Kgf |       Kgf |

-------------------------------------------------

10|  20|        300 |     398.44 |   80.2338 |

20|  30|        300 |     398.44 |   80.2338 |

30|  40|        300 |     398.44 |   80.2338 |

40|  50|        300 |     398.44 |   80.2338 |

50|  60|        300 |     398.44 |   80.2338 |

60|  70|        300 |     398.44 |   80.2338 |

70|Sadl|      462.5 |     398.44 |   123.694 |

Sadl|  80|      462.5 |     398.44 |   123.694 |

70|  80|      462.5 |     398.44 |   123.694 |

80|  90|      462.5 |     398.44 |   123.694 |

-------------------------------------------------

Note:

The Earthquake Loads calculated and printed in the Earthquake

Load calculation report have been factored by the input

scalar/load reduction factor of: 0.700.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Shop/Field Installation Options :

Insulation is installed in the Field before being lifted.

Note : The CG is computed from the first Element From Node

Center of Gravity of the Saddles                           2253.525 mm.

Center of Gravity of the Liquid                            1972.490 mm.

Center of Gravity of the Insulation                        1970.300 mm.

Center of Gravity of the Nozzles                           1775.768 mm.

Center of Gravity of the Added Weights (Operating)         1598.908 mm.

Center of Gravity of the Added Weights (Empty)             1598.908 mm.

Center of Gravity of the Tubesheet(s)                       474.000 mm.

Center of Gravity of the Tubes                             1694.000 mm.

Center of Gravity of Bare Shell New and Cold               1781.005 mm.

Center of Gravity of Bare Shell Corroded                   1725.221 mm.

Vessel CG in the Operating Condition                       1778.494 mm.

Vessel CG in the Fabricated (Shop/Empty) Condition         1723.989 mm.

Vessel CG in the Test Condition                            1861.284 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

ASME VIII Division 2 Horizontal Vessel Analysis, Left Saddle:

Horizontal Vessel Stress Calculations : Operating Case

Warning - Distance to Saddle (a) > 0.25 * Tangent Distance (L) - 4.15.3.2

Input and Calculated Values:

Vessel Mean Radius                            Rm      470.00  mm.

Shell Thickness used in this Case              t      12.000  mm.

Stiffened Vessel Length per 4.15.6             L     3050.00  mm.

Distance from Saddle to Vessel tangent   a1 or a      800.00  mm.

Saddle Width                             b1 or b      140.00  mm.

Saddle Bearing Angle              delta or theta      120.00  degrees

Wear Plate Width                        b2 or b1      300.00  mm.

Wear Plate Bearing Angle        delta2 or theta1      132.00  degrees

Wear Plate Thickness                    e2 or tr        12.0  mm.

Wear Plate Allowable Stress             fw or Sr      137.90  N./mm²

Shell Allowable Stress used in Calculation            137.90  N./mm²

Head Allowable Stress used in Calculation             137.90  N./mm²

Circumferential Efficiency in Plane of Saddle           1.00

Circumferential Efficiency at Mid-Span                  1.00

Distance from Saddle Base to Centerline        B      750.00  mm.

Coefficient of Friction                       mu        0.30

Saddle Force Q, Operating Case                       4522.75  Kgf

Pressure used in Analysis                      P      22.024  bars

Horizontal Vessel Analysis Results:      Actual |    Allowable |

N./mm² |       N./mm² |

----------------------------------------------------------------

Long. Stress at Top    of Midspan         57.52 |       137.90 |

Long. Stress at Bottom of Midspan         57.50 |       137.90 |

Long. Stress at Top    of Saddles         69.08 |       137.90 |

Long. Stress at Bottom of Saddles         51.10 |       137.90 |

----------------------------------------------------------------

Tangential Shear in Shell                  5.84 |       110.32 |

Circ. Stress at Horn of Saddle            12.02 |       172.37 |

Circ. Compressive Stress in Shell          0.67 |       137.90 |

----------------------------------------------------------------

Intermediate Results: Saddle Reaction Q due to Wind or Seismic:

Saddle Reaction Force due to Wind Ft  [Fwt]:

= Ftr( Ft/Num of Saddles + Z Force Load ) * B / E

= 3( 477/2 + 0 ) * 750/843

= 637.0 Kgf

Saddle Reaction Force due to Wind Fl  [Fwl]:

= max( Fl, Sum of X Forces) * B / Ls

= max( 115, 0 ) * 750/1420

= 60.7 Kgf

Saddle Reaction Force due to Earthquake Fl  [Fsl]:

= max( Fl, Sum of X Forces ) * B / Ls

= max( 976, 0 ) * 750/1420

= 515.6 Kgf

Saddle Reaction Force due to Earthquake Ft  [Fst]:

= Ftr( Ft/Num of Saddles + Z Force Load ) * B / E

= 3( 976/2 + 0 ) * 750/843

= 1303.3 Kgf

Load Combination Results for Q + Wind or Seismic [Q]:

= Saddle Load + max( Fwl, Fwt, Fsl, Fst )

= 3219 + max( 60.7, 637, 516, 1303 )

= 4522.7 Kgf

Longitudinal Wind Force [Fl]:

= WindScalar * WindPress( Platform Area + ( End Area * WindDiaMult ) )

= 1 * 1046( 0 +( 0.9 * 1.2 ))

= 1126.093 N

Summary of Loads at the base of this Saddle:

Vertical Load (including saddle weight)              4628.38  Kgf

Transverse Shear Load Saddle           Ft             488.09  Kgf

Longitudinal Shear Load Saddle                        976.18  Kgf

Formulas and Substitutions for Horizontal Vessel Analysis:

Note: Wear Plate is Welded to the Shell, k = 0.1

Saddle Dimension [E]:

= min( 2( ShellID/2 + t + WearPadThickness )sin( theta/2 ), 2*Rm )

= min( 2( 925/2 + 12 + 12 )sin( 120/2 ), 2*470 )

= 842.643 mm.

The Computed K values from Table 4.15.1:

K1  = 0.1066     K2  = 1.1707     K3  = 0.8799     K4  = 0.4011

K5  = 0.7603     K6  = 0.0529     K7  = 0.0529     K8  = 0.3405

K9  = 0.2711     K10 = 0.0581     K1* = 0.1923     K6p = 0.0434

K7p = 0.0434

The suffix 'p' denotes the values for a wear plate if it exists.

Note: Dimension a is greater than or equal to Rm/2.

Moment per Equation 4.15.3 [M1]:

= -Q*a [1 - (1- a/L + (Rm²-h2²)/(2a*L))/(1+(4h2)/3L)]

= -4523*800[1-(1-800/3050+(470²-0²)/

(2*800*3050))/(1+(4*0)/(3*3050))]

= -785.3 Kg-m.

Moment per Equation 4.15.4 [M2]:

= Q*L/4(1+2(Rm²-h2²)/(L²))/(1+(4h2)/( 3L))-4a/L

= 4523*3050/4(1+2(470²-0²)/(3050²))/(1+(4*0)/

(3*3050))-4*800/3050

= -5.8 Kg-m.

Longitudinal Stress at Top of Shell (4.15.6)    [Sigma1]:

= P * Rm/(2t) - M2/(pi*Rm²t)

= 22 * 470/(2*9 ) - -5.82/(pi*470²*9 )

= 57.52 N./mm²

Longitudinal Stress at Bottom of Shell (4.15.7)    [Sigma2]:

= P * Rm/(2t) + M2/(pi * Rm² * t)

= 22 * 470/(2 * 9 ) + -5.82/(pi * 470² * 9 )

= 57.50 N./mm²

Longitudinal Stress at Top of Shell at Support (4.15.10)    [Sigma*3]:

= P * Rm/(2t) - M1/(K1*pi*Rm²t)

= 22*470/(2*9)--785/(0.11*pi*470²*9)

= 69.08 N./mm²

Longitudinal Stress at Bottom of Shell at Support (4.15.11)    [Sigma*4]:

= P * Rm/(2t) + M1/(K1* * pi * Rm² * t)

= 22*470/(2*9)+-785/(0.19*pi*470²*9)

= 51.10 N./mm²

Maximum Shear Force in the Saddle (4.15.5)   [T]:

= Q(L-2a)/(L+(4*h2/3))

= 4523( 3050 - 2 * 800 )/(3050 +( 4 * 0/3))

= 2150.2 Kgf

Shear Stress in the shell no rings,  not stiffened (4.15.14)   [tau2]:

= K2 * T / ( Rm * t )

= 1.17 * 2150/( 470 * 9 )

= 5.84 N./mm²

Decay Length (4.15.22)   [x1,x2]:

= 0.78 * sqrt( Rm * t )

= 0.78 * sqrt( 470 * 9 )

= 50.730 mm.

Effective reinforcing plate width  (4.15.1)   [B1]:

= min( b + 1.56 * sqrt( Rm * t ), 2a  )

= min( 140 + 1.56 * sqrt( 470 * 9 ), 2 * 800 )

= 241.46 mm.

Wear Plate/Shell Stress ratio  (4.15.29)   [eta]:

= min( Sr/S, 1 )

= min( 138/138, 1 )

= 1.0000

Circumferential Stress at Saddle Base with Wear Plate (4.15.26)   [sigma6,r]:

= -K5 * Q * k / ( B1( t + eta * tr ) )

= -0.76 * 4523 * 0.1/( 241( 9 + 1 * 12 ) )

= -0.67 N./mm²

Circ. Comp. Stress at Horn of Saddle, L<8Rm  (4.15.28)   [sigma7,r*]:

= -Q/(4(t+eta*tr)b1) - 12*K7*Q*Rm/(L(t+eta*tr)²)

= -4523/(4(9 + 1 * 12 )241 ) -

12*0.053*4523*470/(3050(9+1*12)²)

= -12.02 N./mm²

Distance between Saddle Supports [Ls]:

= 1420.0 mm.

Free Un-Restrained Thermal Expansion between the Saddles [Exp]:

= Alpha * Ls( Design Temperature - Ambient Temperature )

= 0.12232E-04 * 1420( 120 - 21.1 )

= 1.718 mm.

Results for Vessel Ribs, Web and Base:

Baseplate Length                        Bplen          900.0000  mm.

Baseplate Thickness                     Bpthk           15.0000  mm.

Baseplate Width                         Bpwid          170.0000  mm.

Number of Ribs ( inc. outside ribs )    Nribs                 3

Rib Thickness                           Ribtk           12.0000  mm.

Web Thickness                           Webtk           12.0000  mm.

Web Location                           Webloc            Center

Saddle Yield Stress                        Sy             206.9  N./

Height of Web at Center                  Hw,c             367.5  mm.

Friction Coefficient                       mu             0.300

Note: In the tables below Io is I for the rectangle + Area * Centroid Distance^2

Moment of Inertia of Saddle - Transverse Direction (90 degrees to long axis)

B |           D |           Y |           A |          AY |          Io |

----------------------------------------------------------------------------------------------

Shell            401.0 |         9.0 |         4.5 |        36.1 |     16239.4 |   0.295E+04 |

Wearplate        300.0 |        12.0 |        15.0 |        36.0 |     54000.0 |   0.231E+04 |

Web               12.0 |       248.5 |       145.2 |        29.8 |    433135.5 |   0.229E+04 |

BasePlate        170.0 |        15.0 |       277.0 |        25.5 |    706350.0 |   0.846E+04 |

Totals             ... |         ... |         ... |       127.4 |   1209724.9 |   0.160E+05 |

Distance to Centroid [C1]:

= AY / A

= 476/127

= 94.949 mm.

Angle [beta]:

= 180 - Saddle Angle/2

= 180 - 120/2

= 120.0

Saddle Splitting Coefficient [K1]:

= ( 1 + cos(beta) - 0.5*sin(beta)² )/(pi - beta + sin(beta)cos(beta) )

= ( 1 + cos(120 ) - 0.5*sin(120 )² )/(pi - 2.09 + sin(120 )cos(120 ) )

= 0.2035

Saddle Splitting Force [Fh]:

= K1 * Q

= 0.2 * 4523

= 920.4769 Kgf

Tension Stress, St = ( Fh/As )       =          0.9885  N./mm²

Allowed Stress, Sa = 0.6 * Yield Str =        124.1100  N./mm²

Saddle Splitting Dimension [d]:

= B - R * sin(theta/2)/(theta/2 in radians)

= 750 - 466 * sin(120/2)/1.05

= 365.035 mm.

Bending Moment, M  = Fh * d          =        336.0125  Kg-m.

Bending Stress, Sb = ( M * C1 / I  ) =          1.9548  N./mm²

Allowed Stress, Sa = 2/3 * Yield Str =        137.9000  N./mm²

Minimum Thickness of Baseplate per Moss:

= ( 3( Q + Saddle_Wt )BasePlateWidth / ( 4 * BasePlateLength * AllStress ))½

= ( 3(4523 + 106 )170/( 4 * 900 * 138 ))½

= 6.829 mm.

Calculation of Axial Load, Intermediate Values and Compressive Stress:

Web Length Dimension [ Web Length ]:

= 2 * cos( 90 - Saddle Angle/2 )( Inside Radius + Shell Thk + Wear Plate Thk )

= 2 * cos( 90 - 120/2 )( 462 + 12 + 12 )

= 842.643 mm.

Distance between Ribs [e]:

= Web Length / ( Nribs - 1 )

= 843/( 3 - 1 )

= 421.321 mm.

Baseplate Pressure Area [Ap]:

= e * Bpwid / 2

= 421 * 170/2

= 358.123 cm²

Bearing Pressure [Bp]:

= Q / ( BasePlateLength * BasePlateWidth )

= 4523/( 900 * 170 )

= 2.956 Kgf/cm²

Axial Load [P]:

= Ap * Bp

= 358 * 2.96

= 1058.628 Kgf

Area of the Rib and Web [Ar]:

= Rib Area + Web Area

= 15.4 + 25.3

= 40.639 cm²

Compressive Stress [Sc]:

= P/Ar

= 1059/40.6

= 2.555 N./mm²

Check of Outside Ribs:

Inertia of Saddle, Outer Ribs - Longitudinal Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib+Web        12.0 |       140.0 |         ... |        16.8 |         ... |    274.     |

Rib dimension [D]:

= Saddle Width - Web Thickness

= 140 - 12

= 128.000 mm.

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/40.6

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 274/40.6 )

= 25.985 mm.

Length of Outer Rib [L]:

= Saddle Height - cos( theta/2 )( radius + shlthk + wpdthk ) - bpthk

= 750 - cos( 120/2 )( 462 + 12 + 12 ) - 15

= 491.750 mm.

Intermediate Term [Cc]:

= sqrt( 2 * pi² * Elastic Modulus / Yield Stress )

= sqrt( 2 * pi² * 199943008/207 )

= 138.135

Slenderness ratio [KL/r]:

= KL/r

= 1 * 492/26

= 18.925

Bending Moment [Rm]:

= Fl /( 2 * Bplen ) * e * L / 2

= 976/( 2 * 900 ) * 421 * 492/2

= 56.181 Kg-m.

Compressive Allowable, KL/r < Cc( 18.9 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 18.9 )²/(2 * 138² ))207/

( 5/3+3*(18.9 )/(8* 138 )-( 18.9³)/(8*138³)

= 119.3 N./mm²

AISC Unity Check of Outside Ribs ( must be <= 1 )

= Sc/Sca + ( Rm * C1 / I )/Sba

= 2.55/119 +( 56.2 * 70/2744000 )/138

= 0.123

Check of Inside Ribs:

Inertia of Saddle, Inner Ribs - Axial Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib            12.0 |       128.0 |         0.0 |        15.4 |         0.0 |    274.     |

Web           421.3 |        12.0 |         0.0 |        50.6 |         0.0 |    6.07     |

Totals          ... |         ... |         ... |        65.9 |         ... |    280.     |

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/65.9

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Length of Inner Rib [L]:

= Saddle Height - Outside Radius - Bpthk

= 750 - cos( 486/2 )( 15 + 0 + 0 ) - 0

= 248.500 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 280/65.9 )

= 20.621 mm.

Slenderness ratio [KL/r]:

= KL/r

= 1 * 248/20.6

= 12.051

Unit Force [Force,u]:

= Fl / ( 2 * Baseplate Length )

= 976/( 2 * 900 )

= 0.542 Kgf/mm.

Moment at base of inner Rib [Mbase,c]:

= Unit Force * e * L

= 0.54 * 421 * 248

= 56.781 Kg-m.

Bending Stress due to Transverse Force and Weight Load [SigmaB,base,c]:

= Bending Moment / Section Modulus

= 56.8/40042

= 13.906 N./mm²

Compressive Allowable, KL/r < Cc( 12.1 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 12.1 )²/(2 * 138² ))207/

( 5/3+3*(12.1 )/(8* 138 )-( 12.1³)/(8*138³)

= 121.3 N./mm²

AISC Unity Check of Inside Ribs ( must be <= 1 )

= Sc/Sca + ( Mbase,c * C1/I )/Sba

= 3.12/121 +( 56.8 * 70/280 )/138

= 0.127

Warning: bolt dia. 20.000 not found in database, using 19.050 mm.

Input Data for Base Plate Bolting Calculations:

Total Number of Bolts per BasePlate            Nbolts           4

Total Number of Bolts in Tension/Baseplate        Nbt           2

Bolt Material Specification                             SA-193 B7

Bolt Allowable Stress                            Stba      283.00  N./mm²

Bolt Corrosion Allowance                          Bca         0.0  mm.

Distance from Bolts to Edge                   Edgedis       120.0  mm.

Nominal Bolt Diameter                             Bnd     19.0500  mm.

Thread Series                                  Series          TEMA

BasePlate Allowable Stress                          S      108.25  N./mm²

Area Available in a Single Bolt               BltArea      1.9484  cm²

Saddle Load QO (Weight)                            QO      3325.1  Kgf

Saddle Load QL (Wind/Seismic contribution)         QL       515.6  Kgf

Maximum Transverse Force                           Ft       488.1  Kgf

Maximum Longitudinal Force                         Fl       976.2  Kgf

Saddle Bolted to Steel Foundation                          No

Shear Stress in a Single Bolt, Longitudinal Direction [taub,l]:

= Fl / ( Bolt Area * Number of Bolts )

= 976/( 1.95 * 4 )

= 12.3 N./mm².  Must be less than 146.2 N./mm².

Shear Stress in a Single Bolt, Transverse Direction [taub,t]:

= Ft / ( Bolt Area * Number of Bolts )

= 488/( 1.95 * 4 )

= 6.1 N./mm².  Must be less than 146.2 N./mm².

Bolt Area Calculation per Dennis R. Moss

Bolt Area Requirement Due to Longitudinal Load [Bltarearl]:

= 0.0 (QO > QL --> No Uplift in Longitudinal direction)

Bolt Area due to Shear Load [Bltarears]:

= Fl / ( BoltShearAllowable * Nbolts )

= 976/(146 * 4 )

= 0.1637 cm²

Bolt Area due to Transverse Load:

Moment on Baseplate Due to Transverse Load [Rmom]:

= B * Ft + Sum of X Moments

= 750 * 488 + 0

= 366.07 Kg-m.

Eccentricity (e):

= Rmom / QO

= 366/3325

= 110.09 mm. < Bplen/6 --> No Uplift in Transverse direction

Bolt Area due to Transverse Load [Bltareart]:

= 0 (No Uplift)

Required Area of a Single Bolt [Bltarear]:

= max[Bltarearl, Bltarears, Bltareart]

= max[0, 0.16, 0 ]

= 0.1637 cm²

ASME VIII Division 2 Horizontal Vessel Analysis, Right Saddle:

Input and Calculated Values:

Vessel Mean Radius                            Rm      470.00  mm.

Shell Thickness used in this Case              t      12.000  mm.

Stiffened Vessel Length per 4.15.6             L     3050.00  mm.

Distance from Saddle to Vessel tangent   a1 or a      600.00  mm.

Saddle Width                             b1 or b      140.00  mm.

Saddle Bearing Angle              delta or theta      120.00  degrees

Wear Plate Width                        b2 or b1      300.00  mm.

Wear Plate Bearing Angle        delta2 or theta1      132.00  degrees

Wear Plate Thickness                    e2 or tr        12.0  mm.

Wear Plate Allowable Stress             fw or Sr      137.90  N./mm²

Inside Depth of Head                    Hi or h2      234.25  mm.

Shell Allowable Stress used in Calculation            137.90  N./mm²

Head Allowable Stress used in Calculation             137.90  N./mm²

Circumferential Efficiency in Plane of Saddle           1.00

Circumferential Efficiency at Mid-Span                  1.00

Distance from Saddle Base to Centerline        B      750.00  mm.

Coefficient of Friction                       mu        0.30

Saddle Force Q, Operating Case                       1856.95  Kgf

Pressure used in Analysis                      P      22.024  bars

Horizontal Vessel Analysis Results:      Actual |    Allowable |

N./mm² |       N./mm² |

----------------------------------------------------------------

Long. Stress at Top    of Midspan         57.17 |       137.90 |

Long. Stress at Bottom of Midspan         57.85 |       137.90 |

Long. Stress at Top    of Saddles         61.29 |       137.90 |

Long. Stress at Bottom of Saddles         55.42 |       137.90 |

----------------------------------------------------------------

Tangential Shear in Shell                  2.77 |       110.32 |

Circ. Stress at Horn of Saddle             4.93 |       172.37 |

Circ. Compressive Stress in Shell          0.27 |       137.90 |

----------------------------------------------------------------

Intermediate Results: Saddle Reaction Q due to Wind or Seismic:

Saddle Reaction Force due to Wind Ft  [Fwt]:

= Ftr( Ft/Num of Saddles + Z Force Load ) * B / E

= 3( 477/2 + 0 ) * 750/843

= 637.0 Kgf

Saddle Reaction Force due to Wind Fl  [Fwl]:

= max( Fl, Sum of X Forces) * B / Ls

= max( 115, 0 ) * 750/1420

= 60.7 Kgf

Saddle Reaction Force due to Earthquake Fl  [Fsl]:

= max( Fl, Sum of X Forces ) * B / Ls

= max( 976, 0 ) * 750/1420

= 515.6 Kgf

Saddle Reaction Force due to Earthquake Ft  [Fst]:

= Ftr( Ft/Num of Saddles + Z Force Load ) * B / E

= 3( 976/2 + 0 ) * 750/843

= 1303.3 Kgf

Load Combination Results for Q + Wind or Seismic [Q]:

= Saddle Load + max( Fwl, Fwt, Fsl, Fst )

= 554 + max( 60.7, 637, 516, 1303 )

= 1856.9 Kgf

Longitudinal Wind Force [Fl]:

= WindScalar * WindPress( Platform Area + ( End Area * WindDiaMult ) )

= 1 * 1046( 0 +( 0.9 * 1.2 ))

= 1126.093 N

Summary of Loads at the base of this Saddle:

Vertical Load (including saddle weight)              1962.58  Kgf

Transverse Shear Load Saddle           Ft             488.09  Kgf

Longitudinal Shear Load Saddle                        976.18  Kgf

Formulas and Substitutions for Horizontal Vessel Analysis:

Note: Wear Plate is Welded to the Shell, k = 0.1

Saddle Dimension [E]:

= min( 2( ShellID/2 + t + WearPadThickness )sin( theta/2 ), 2*Rm )

= min( 2( 925/2 + 12 + 12 )sin( 120/2 ), 2*470 )

= 842.643 mm.

The Computed K values from Table 4.15.1:

K1  = 0.1066     K2  = 1.1707     K3  = 0.8799     K4  = 0.4011

K5  = 0.7603     K6  = 0.0529     K7  = 0.0529     K8  = 0.3405

K9  = 0.2711     K10 = 0.0581     K1* = 0.1923     K6p = 0.0434

K7p = 0.0434

The suffix 'p' denotes the values for a wear plate if it exists.

Note: Dimension a is greater than or equal to Rm/2.

Moment per Equation 4.15.3 [M1]:

= -Q*a [1 - (1- a/L + (Rm²-h2²)/(2a*L))/(1+(4h2)/3L)]

= -1857*600[1-(1-600/3050+(470²-234²)/

(2*600*3050))/(1+(4*234)/(3*3050))]

= -256.5 Kg-m.

Moment per Equation 4.15.4 [M2]:

= Q*L/4(1+2(Rm²-h2²)/(L²))/(1+(4h2)/( 3L))-4a/L

= 1857*3050/4(1+2(470²-234²)/(3050²))/(1+(4*234)/

(3*3050))-4*600/3050

= 216.1 Kg-m.

Longitudinal Stress at Top of Shell (4.15.6)    [Sigma1]:

= P * Rm/(2t) - M2/(pi*Rm²t)

= 22 * 470/(2*9 ) - 216/(pi*470²*9 )

= 57.17 N./mm²

Longitudinal Stress at Bottom of Shell (4.15.7)    [Sigma2]:

= P * Rm/(2t) + M2/(pi * Rm² * t)

= 22 * 470/(2 * 9 ) + 216/(pi * 470² * 9 )

= 57.85 N./mm²

Longitudinal Stress at Top of Shell at Support (4.15.10)    [Sigma*3]:

= P * Rm/(2t) - M1/(K1*pi*Rm²t)

= 22*470/(2*9)--256/(0.11*pi*470²*9)

= 61.29 N./mm²

Longitudinal Stress at Bottom of Shell at Support (4.15.11)    [Sigma*4]:

= P * Rm/(2t) + M1/(K1* * pi * Rm² * t)

= 22*470/(2*9)+-256/(0.19*pi*470²*9)

= 55.42 N./mm²

Maximum Shear Force in the Saddle (4.15.5)   [T]:

= Q(L-2a)/(L+(4*h2/3))

= 1857( 3050 - 2 * 600 )/(3050 +( 4 * 234/3))

= 1021.7 Kgf

Shear Stress in the shell no rings,  not stiffened (4.15.14)   [tau2]:

= K2 * T / ( Rm * t )

= 1.17 * 1022/( 470 * 9 )

= 2.77 N./mm²

Decay Length (4.15.22)   [x1,x2]:

= 0.78 * sqrt( Rm * t )

= 0.78 * sqrt( 470 * 9 )

= 50.730 mm.

Effective reinforcing plate width  (4.15.1)   [B1]:

= min( b + 1.56 * sqrt( Rm * t ), 2a  )

= min( 140 + 1.56 * sqrt( 470 * 9 ), 2 * 600 )

= 241.46 mm.

Wear Plate/Shell Stress ratio  (4.15.29)   [eta]:

= min( Sr/S, 1 )

= min( 138/138, 1 )

= 1.0000

Circumferential Stress at Saddle Base with Wear Plate (4.15.26)   [sigma6,r]:

= -K5 * Q * k / ( B1( t + eta * tr ) )

= -0.76 * 1857 * 0.1/( 241( 9 + 1 * 12 ) )

= -0.27 N./mm²

Circ. Comp. Stress at Horn of Saddle, L<8Rm  (4.15.28)   [sigma7,r*]:

= -Q/(4(t+eta*tr)b1) - 12*K7*Q*Rm/(L(t+eta*tr)²)

= -1857/(4(9 + 1 * 12 )241 ) -

12*0.053*1857*470/(3050(9+1*12)²)

= -4.93 N./mm²

Results for Vessel Ribs, Web and Base:

Baseplate Length                        Bplen          900.0000  mm.

Baseplate Thickness                     Bpthk           15.0000  mm.

Baseplate Width                         Bpwid          170.0000  mm.

Number of Ribs ( inc. outside ribs )    Nribs                 3

Rib Thickness                           Ribtk           12.0000  mm.

Web Thickness                           Webtk           12.0000  mm.

Web Location                           Webloc            Center

Saddle Yield Stress                        Sy             206.9  N./

Height of Web at Center                  Hw,c             367.5  mm.

Friction Coefficient                       mu             0.300

Note: In the tables below Io is I for the rectangle + Area * Centroid Distance^2

Moment of Inertia of Saddle - Transverse Direction (90 degrees to long axis)

B |           D |           Y |           A |          AY |          Io |

----------------------------------------------------------------------------------------------

Shell            401.0 |         9.0 |         4.5 |        36.1 |     16239.4 |   0.295E+04 |

Wearplate        300.0 |        12.0 |        15.0 |        36.0 |     54000.0 |   0.231E+04 |

Web               12.0 |       248.5 |       145.2 |        29.8 |    433135.5 |   0.229E+04 |

BasePlate        170.0 |        15.0 |       277.0 |        25.5 |    706350.0 |   0.846E+04 |

Totals             ... |         ... |         ... |       127.4 |   1209724.9 |   0.160E+05 |

Distance to Centroid [C1]:

= AY / A

= 476/127

= 94.949 mm.

Angle [beta]:

= 180 - Saddle Angle/2

= 180 - 120/2

= 120.0

Saddle Splitting Coefficient [K1]:

= ( 1 + cos(beta) - 0.5*sin(beta)² )/(pi - beta + sin(beta)cos(beta) )

= ( 1 + cos(120 ) - 0.5*sin(120 )² )/(pi - 2.09 + sin(120 )cos(120 ) )

= 0.2035

Saddle Splitting Force [Fh]:

= K1 * Q

= 0.2 * 1857

= 377.9294 Kgf

Tension Stress, St = ( Fh/As )       =          0.4059  N./mm²

Allowed Stress, Sa = 0.6 * Yield Str =        124.1100  N./mm²

Saddle Splitting Dimension [d]:

= B - R * sin(theta/2)/(theta/2 in radians)

= 750 - 466 * sin(120/2)/1.05

= 365.035 mm.

Bending Moment, M  = Fh * d          =        137.9600  Kg-m.

Bending Stress, Sb = ( M * C1 / I  ) =          0.8026  N./mm²

Allowed Stress, Sa = 2/3 * Yield Str =        137.9000  N./mm²

Minimum Thickness of Baseplate per Moss:

= ( 3( Q + Saddle_Wt )BasePlateWidth / ( 4 * BasePlateLength * AllStress ))½

= ( 3(1857 + 106 )170/( 4 * 900 * 138 ))½

= 4.447 mm.

Calculation of Axial Load, Intermediate Values and Compressive Stress:

Web Length Dimension [ Web Length ]:

= 2 * cos( 90 - Saddle Angle/2 )( Inside Radius + Shell Thk + Wear Plate Thk )

= 2 * cos( 90 - 120/2 )( 462 + 12 + 12 )

= 842.643 mm.

Distance between Ribs [e]:

= Web Length / ( Nribs - 1 )

= 843/( 3 - 1 )

= 421.321 mm.

Baseplate Pressure Area [Ap]:

= e * Bpwid / 2

= 421 * 170/2

= 358.123 cm²

Bearing Pressure [Bp]:

= Q / ( BasePlateLength * BasePlateWidth )

= 1857/( 900 * 170 )

= 1.214 Kgf/cm²

Axial Load [P]:

= Ap * Bp

= 358 * 1.21

= 434.651 Kgf

Area of the Rib and Web [Ar]:

= Rib Area + Web Area

= 15.4 + 25.3

= 40.639 cm²

Compressive Stress [Sc]:

= P/Ar

= 435/40.6

= 1.049 N./mm²

Check of Outside Ribs:

Inertia of Saddle, Outer Ribs - Longitudinal Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib+Web        12.0 |       140.0 |         ... |        16.8 |         ... |    274.     |

Rib dimension [D]:

= Saddle Width - Web Thickness

= 140 - 12

= 128.000 mm.

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/40.6

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 274/40.6 )

= 25.985 mm.

Length of Outer Rib [L]:

= Saddle Height - cos( theta/2 )( radius + shlthk + wpdthk ) - bpthk

= 750 - cos( 120/2 )( 462 + 12 + 12 ) - 15

= 491.750 mm.

Intermediate Term [Cc]:

= sqrt( 2 * pi² * Elastic Modulus / Yield Stress )

= sqrt( 2 * pi² * 199943008/207 )

= 138.135

Slenderness ratio [KL/r]:

= KL/r

= 1 * 492/26

= 18.925

Bending Moment [Rm]:

= Fl /( 2 * Bplen ) * e * L / 2

= 976/( 2 * 900 ) * 421 * 492/2

= 56.181 Kg-m.

Compressive Allowable, KL/r < Cc( 18.9 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 18.9 )²/(2 * 138² ))207/

( 5/3+3*(18.9 )/(8* 138 )-( 18.9³)/(8*138³)

= 119.3 N./mm²

AISC Unity Check of Outside Ribs ( must be <= 1 )

= Sc/Sca + ( Rm * C1 / I )/Sba

= 1.05/119 +( 56.2 * 70/2744000 )/138

= 0.111

Check of Inside Ribs:

Inertia of Saddle, Inner Ribs - Axial Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib            12.0 |       128.0 |         0.0 |        15.4 |         0.0 |    274.     |

Web           421.3 |        12.0 |         0.0 |        50.6 |         0.0 |    6.07     |

Totals          ... |         ... |         ... |        65.9 |         ... |    280.     |

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/65.9

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Length of Inner Rib [L]:

= Saddle Height - Outside Radius - Bpthk

= 750 - cos( 486/2 )( 15 + 0 + 0 ) - 0

= 248.500 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 280/65.9 )

= 20.621 mm.

Slenderness ratio [KL/r]:

= KL/r

= 1 * 248/20.6

= 12.051

Unit Force [Force,u]:

= Fl / ( 2 * Baseplate Length )

= 976/( 2 * 900 )

= 0.542 Kgf/mm.

Moment at base of inner Rib [Mbase,c]:

= Unit Force * e * L

= 0.54 * 421 * 248

= 56.781 Kg-m.

Bending Stress due to Transverse Force and Weight Load [SigmaB,base,c]:

= Bending Moment / Section Modulus

= 56.8/40042

= 13.906 N./mm²

Compressive Allowable, KL/r < Cc( 12.1 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 12.1 )²/(2 * 138² ))207/

( 5/3+3*(12.1 )/(8* 138 )-( 12.1³)/(8*138³)

= 121.3 N./mm²

AISC Unity Check of Inside Ribs ( must be <= 1 )

= Sc/Sca + ( Mbase,c * C1/I )/Sba

= 1.28/121 +( 56.8 * 70/280 )/138

= 0.111

Warning: bolt dia. 20.000 not found in database, using 19.050 mm.

Input Data for Base Plate Bolting Calculations:

Total Number of Bolts per BasePlate            Nbolts           4

Total Number of Bolts in Tension/Baseplate        Nbt           2

Bolt Material Specification                             SA-193 B7

Bolt Allowable Stress                            Stba      283.00  N./mm²

Bolt Corrosion Allowance                          Bca         0.0  mm.

Distance from Bolts to Edge                   Edgedis       120.0  mm.

Nominal Bolt Diameter                             Bnd     19.0500  mm.

Thread Series                                  Series          TEMA

BasePlate Allowable Stress                          S      108.25  N./mm²

Area Available in a Single Bolt               BltArea      1.9484  cm²

Saddle Load QO (Weight)                            QO       659.3  Kgf

Saddle Load QL (Wind/Seismic contribution)         QL       515.6  Kgf

Maximum Transverse Force                           Ft       488.1  Kgf

Maximum Longitudinal Force                         Fl       976.2  Kgf

Saddle Bolted to Steel Foundation                          No

Shear Stress in a Single Bolt, Longitudinal Direction [taub,l]:

= Fl / ( Bolt Area * Number of Bolts )

= 976/( 1.95 * 4 )

= 12.3 N./mm².  Must be less than 146.2 N./mm².

Shear Stress in a Single Bolt, Transverse Direction [taub,t]:

= Ft / ( Bolt Area * Number of Bolts )

= 488/( 1.95 * 4 )

= 6.1 N./mm².  Must be less than 146.2 N./mm².

Bolt Area Calculation per Dennis R. Moss

Bolt Area Requirement Due to Longitudinal Load [Bltarearl]:

= 0.0 (QO > QL --> No Uplift in Longitudinal direction)

Bolt Area due to Shear Load [Bltarears]:

= Fl / ( BoltShearAllowable * Nbolts )

= 976/(146 * 4 )

= 0.1637 cm²

Bolt Area due to Transverse Load:

Moment on Baseplate Due to Transverse Load [Rmom]:

= B * Ft + Sum of X Moments

= 750 * 488 + 0

= 366.07 Kg-m.

Eccentricity (e):

= Rmom / QO

= 366/659

= 555.23 mm. > Bplen/6 --> Uplift in Transverse direction

f = Bplen / 2 - Edgedis

= 900/2 - 120

= 330.00 mm.

Modular Ratio Of Steel/Concrete (n1):

= ES / EC

= 203402/21526

= 9.45

K1 = 3 (e - 0.5 * Bplen)

= 3(555 - 0.5*900 )

= 315.70 mm.

K2 = 6 * n1 * At / Bpwid * (f + e)

= 6 * 9.45 * 3.9/170 *(330 + 555 )

= 115040.72 mm.²

K3 = -K2 * (0.5 * Bplen + f)

= -115041 *(0.5 * 900 + 330 )

= -89731751.59 mm.³

Iteratively Solving for the Effective Bearing Length:

Y³ + K1 * Y² + K2 * Y + K3 = 0

Y³ + 316 * Y² + 115041 * Y + -89731752 = 0

Y  = 299.66 mm.

Num = (Bplen / 2 - Y / 3 - e)

= (900/2 - 300/3 - 555 )

= -205.12

Denom = (Bplen / 2 - Y / 3 + f)

= (900/2 - 300/3 + 330 )

= 680.11

Total Bolt Tension Force [Tforce]:

= - QO * Num / Denom

= - 659 * -205/680

= 198.85 Kgf

Bolt Area Required due to Transverse Load [Bltareart]:

= Tforce / (Stba * Nbt)

= 199/( 283 * 2 )

= 0.0345 cm²

Required Area of a Single Bolt [Bltarear]:

= max[Bltarearl, Bltarears, Bltareart]

= max[0, 0.16, 0.034 ]

= 0.1637 cm²

Baseplate Thickness Calculation per D. Moss:

Bearing Pressure (fc)

= 2(QO + Tforce) / (Y * Bpwid)

= 2(659 + 199 )/(300 * 170 )

= 3.30 bars

Distance from Baseplate Edge to the Web [ADIST]:

= (Bplen - Weblngth) / 2

= (900 - 849 )/2

= 25.4000 mm.

Overturning Moment due To Bolt Tension [Mt]:

= Tforce * Adist

= 199 * 25.4

= 5.05 Kg-m.

Equivalent Bearing Pressure (f1):

= fc * (Y - Adist) / Y

= 3.3 *(300 - 25.4 )/300

= 3.02 bars

Overturning Moment due to Bearing Pressure [Mc]:

= (Adist² * Bpwid / 6) * (f1 + 2 * fc)

= (25.4² * 170/6) *(3.02 + 2 * 3.3 )

= 1.80 Kg-m.

Baseplate Required Thickness [Treq]:

= (6 * max(Mt,Mc) / (Bpwid * Sba))½

= (6 *max(5.05,1.8/(170 * 162 ))½

= 3.2811 mm.

Warning:

Please note that nozzle loadings, if included, are assumed to be local in nature

and will not contribute to or create a net section bending moment.  Therefore, the

addition of nozzle loads will not affect the support load calculation.  If you wish

to create a load on the legs/lugs etc. from forces or moments, use the Force/Moment dialog

and add the appropriate forces and moments at the correct locations in the model. Ensure

that all supports are designed to take into account all possible loading conditions.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

ASME VIII Division 2 Horizontal Vessel Analysis, Left Saddle:

Horizontal Vessel Stress Calculations : Test Case

Warning - Distance to Saddle (a) > 0.25 * Tangent Distance (L) - 4.15.3.2

Input and Calculated Values:

Vessel Mean Radius                            Rm      470.00  mm.

Shell Thickness used in this Case              t      12.000  mm.

Stiffened Vessel Length per 4.15.6             L     3050.00  mm.

Distance from Saddle to Vessel tangent   a1 or a      800.00  mm.

Saddle Width                             b1 or b      140.00  mm.

Saddle Bearing Angle              delta or theta      120.00  degrees

Wear Plate Width                        b2 or b1      300.00  mm.

Wear Plate Bearing Angle        delta2 or theta1      132.00  degrees

Wear Plate Thickness                    e2 or tr        12.0  mm.

Wear Plate Allowable Stress             fw or Sr      137.90  N./mm²

Shell Allowable Stress used in Calculation            235.81  N./mm²

Head Allowable Stress used in Calculation             235.81  N./mm²

Circumferential Efficiency in Plane of Saddle           1.00

Circumferential Efficiency at Mid-Span                  1.00

Distance from Saddle Base to Centerline        B      750.00  mm.

Coefficient of Friction                       mu        0.30

Saddle Force Q, Test Case, no Ext. Forces            3894.82  Kgf

Pressure used in Analysis                      P      28.646  bars

Horizontal Vessel Analysis Results:      Actual |    Allowable |

N./mm² |       N./mm² |

----------------------------------------------------------------

Long. Stress at Top    of Midspan         74.81 |       235.81 |

Long. Stress at Bottom of Midspan         74.79 |       235.81 |

Long. Stress at Top    of Saddles         84.76 |       235.81 |

Long. Stress at Bottom of Saddles         69.28 |       235.81 |

----------------------------------------------------------------

Tangential Shear in Shell                  5.03 |       139.65 |

Circ. Stress at Horn of Saddle            10.35 |       353.71 |

Circ. Compressive Stress in Shell          0.57 |       235.81 |

----------------------------------------------------------------

Intermediate Results: Saddle Reaction Q due to Wind or Seismic:

Saddle Reaction Force due to Wind Ft  [Fwt]:

= Ftr( Ft/Num of Saddles + Z Force Load ) * B / E

= 3( 157/2 + 0 ) * 750/843

= 210.2 Kgf

Saddle Reaction Force due to Wind Fl  [Fwl]:

= max( Fl, Sum of X Forces) * B / Ls

= max( 37.9, 0 ) * 750/1420

= 20.0 Kgf

Load Combination Results for Q + Wind or Seismic [Q]:

= Saddle Load + max( Fwl, Fwt, Fsl, Fst )

= 3685 + max( 20, 210, 0, 0 )

= 3894.8 Kgf

Longitudinal Wind Force [Fl]:

= WindScalar * WindPress( Platform Area + ( End Area * WindDiaMult ) )

= 1 * 1046( 0 +( 0.9 * 1.2 ))

= 1126.093 N

Summary of Loads at the base of this Saddle:

Vertical Load (including saddle weight)              4000.46  Kgf

Transverse Shear Load Saddle           Ft              78.72  Kgf

Longitudinal Shear Load Saddle                         37.89  Kgf

Formulas and Substitutions for Horizontal Vessel Analysis:

Note: Wear Plate is Welded to the Shell, k = 0.1

Saddle Dimension [E]:

= min( 2( ShellID/2 + t + WearPadThickness )sin( theta/2 ), 2*Rm )

= min( 2( 925/2 + 12 + 12 )sin( 120/2 ), 2*470 )

= 842.643 mm.

The Computed K values from Table 4.15.1:

K1  = 0.1066     K2  = 1.1707     K3  = 0.8799     K4  = 0.4011

K5  = 0.7603     K6  = 0.0529     K7  = 0.0529     K8  = 0.3405

K9  = 0.2711     K10 = 0.0581     K1* = 0.1923     K6p = 0.0434

K7p = 0.0434

The suffix 'p' denotes the values for a wear plate if it exists.

Note: Dimension a is greater than or equal to Rm/2.

Moment per Equation 4.15.3 [M1]:

= -Q*a [1 - (1- a/L + (Rm²-h2²)/(2a*L))/(1+(4h2)/3L)]

= -3895*800[1-(1-800/3050+(470²-0²)/

(2*800*3050))/(1+(4*0)/(3*3050))]

= -676.2 Kg-m.

Moment per Equation 4.15.4 [M2]:

= Q*L/4(1+2(Rm²-h2²)/(L²))/(1+(4h2)/( 3L))-4a/L

= 3895*3050/4(1+2(470²-0²)/(3050²))/(1+(4*0)/

(3*3050))-4*800/3050

= -5.0 Kg-m.

Longitudinal Stress at Top of Shell (4.15.6)    [Sigma1]:

= P * Rm/(2t) - M2/(pi*Rm²t)

= 28.6 * 470/(2*9 ) - -5.01/(pi*470²*9 )

= 74.81 N./mm²

Longitudinal Stress at Bottom of Shell (4.15.7)    [Sigma2]:

= P * Rm/(2t) + M2/(pi * Rm² * t)

= 28.6 * 470/(2 * 9 ) + -5.01/(pi * 470² * 9 )

= 74.79 N./mm²

Longitudinal Stress at Top of Shell at Support (4.15.10)    [Sigma*3]:

= P * Rm/(2t) - M1/(K1*pi*Rm²t)

= 28.6*470/(2*9)--676/(0.11*pi*470²*9)

= 84.76 N./mm²

Longitudinal Stress at Bottom of Shell at Support (4.15.11)    [Sigma*4]:

= P * Rm/(2t) + M1/(K1* * pi * Rm² * t)

= 28.6*470/(2*9)+-676/(0.19*pi*470²*9)

= 69.28 N./mm²

Maximum Shear Force in the Saddle (4.15.5)   [T]:

= Q(L-2a)/(L+(4*h2/3))

= 3895( 3050 - 2 * 800 )/(3050 +( 4 * 0/3))

= 1851.6 Kgf

Shear Stress in the shell no rings,  not stiffened (4.15.14)   [tau2]:

= K2 * T / ( Rm * t )

= 1.17 * 1852/( 470 * 9 )

= 5.03 N./mm²

Decay Length (4.15.22)   [x1,x2]:

= 0.78 * sqrt( Rm * t )

= 0.78 * sqrt( 470 * 9 )

= 50.730 mm.

Effective reinforcing plate width  (4.15.1)   [B1]:

= min( b + 1.56 * sqrt( Rm * t ), 2a  )

= min( 140 + 1.56 * sqrt( 470 * 9 ), 2 * 800 )

= 241.46 mm.

Wear Plate/Shell Stress ratio  (4.15.29)   [eta]:

= 1.0000 Materials are the same, test case

Circumferential Stress at Saddle Base with Wear Plate (4.15.26)   [sigma6,r]:

= -K5 * Q * k / ( B1( t + eta * tr ) )

= -0.76 * 3895 * 0.1/( 241( 9 + 1 * 12 ) )

= -0.57 N./mm²

Circ. Comp. Stress at Horn of Saddle, L<8Rm  (4.15.28)   [sigma7,r*]:

= -Q/(4(t+eta*tr)b1) - 12*K7*Q*Rm/(L(t+eta*tr)²)

= -3895/(4(9 + 1 * 12 )241 ) -

12*0.053*3895*470/(3050(9+1*12)²)

= -10.35 N./mm²

Results for Vessel Ribs, Web and Base:

Baseplate Length                        Bplen          900.0000  mm.

Baseplate Thickness                     Bpthk           15.0000  mm.

Baseplate Width                         Bpwid          170.0000  mm.

Number of Ribs ( inc. outside ribs )    Nribs                 3

Rib Thickness                           Ribtk           12.0000  mm.

Web Thickness                           Webtk           12.0000  mm.

Web Location                           Webloc            Center

Saddle Yield Stress                        Sy             206.9  N./

Height of Web at Center                  Hw,c             367.5  mm.

Friction Coefficient                       mu             0.300

Note: In the tables below Io is I for the rectangle + Area * Centroid Distance^2

Moment of Inertia of Saddle - Transverse Direction (90 degrees to long axis)

B |           D |           Y |           A |          AY |          Io |

----------------------------------------------------------------------------------------------

Shell            401.0 |         9.0 |         4.5 |        36.1 |     16239.4 |   0.295E+04 |

Wearplate        300.0 |        12.0 |        15.0 |        36.0 |     54000.0 |   0.231E+04 |

Web               12.0 |       248.5 |       145.2 |        29.8 |    433135.5 |   0.229E+04 |

BasePlate        170.0 |        15.0 |       277.0 |        25.5 |    706350.0 |   0.846E+04 |

Totals             ... |         ... |         ... |       127.4 |   1209724.9 |   0.160E+05 |

Distance to Centroid [C1]:

= AY / A

= 476/127

= 94.949 mm.

Angle [beta]:

= 180 - Saddle Angle/2

= 180 - 120/2

= 120.0

Saddle Splitting Coefficient [K1]:

= ( 1 + cos(beta) - 0.5*sin(beta)² )/(pi - beta + sin(beta)cos(beta) )

= ( 1 + cos(120 ) - 0.5*sin(120 )² )/(pi - 2.09 + sin(120 )cos(120 ) )

= 0.2035

Saddle Splitting Force [Fh]:

= K1 * Q

= 0.2 * 3895

= 792.6811 Kgf

Tension Stress, St = ( Fh/As )       =          0.8513  N./mm²

Allowed Stress, Sa = 0.6 * Yield Str =        124.1100  N./mm²

Saddle Splitting Dimension [d]:

= B - R * sin(theta/2)/(theta/2 in radians)

= 750 - 466 * sin(120/2)/1.05

= 365.035 mm.

Bending Moment, M  = Fh * d          =        289.3617  Kg-m.

Bending Stress, Sb = ( M * C1 / I  ) =          1.6834  N./mm²

Allowed Stress, Sa = 2/3 * Yield Str =        137.9000  N./mm²

Minimum Thickness of Baseplate per Moss:

= ( 3( Q + Saddle_Wt )BasePlateWidth / ( 4 * BasePlateLength * AllStress ))½

= ( 3(3895 + 106 )170/( 4 * 900 * 138 ))½

= 6.348 mm.

Calculation of Axial Load, Intermediate Values and Compressive Stress:

Web Length Dimension [ Web Length ]:

= 2 * cos( 90 - Saddle Angle/2 )( Inside Radius + Shell Thk + Wear Plate Thk )

= 2 * cos( 90 - 120/2 )( 462 + 12 + 12 )

= 842.643 mm.

Distance between Ribs [e]:

= Web Length / ( Nribs - 1 )

= 843/( 3 - 1 )

= 421.321 mm.

Baseplate Pressure Area [Ap]:

= e * Bpwid / 2

= 421 * 170/2

= 358.123 cm²

Bearing Pressure [Bp]:

= Q / ( BasePlateLength * BasePlateWidth )

= 3895/( 900 * 170 )

= 2.546 Kgf/cm²

Axial Load [P]:

= Ap * Bp

= 358 * 2.55

= 911.651 Kgf

Area of the Rib and Web [Ar]:

= Rib Area + Web Area

= 15.4 + 25.3

= 40.639 cm²

Compressive Stress [Sc]:

= P/Ar

= 912/40.6

= 2.200 N./mm²

Check of Outside Ribs:

Inertia of Saddle, Outer Ribs - Longitudinal Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib+Web        12.0 |       140.0 |         ... |        16.8 |         ... |    274.     |

Rib dimension [D]:

= Saddle Width - Web Thickness

= 140 - 12

= 128.000 mm.

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/40.6

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 274/40.6 )

= 25.985 mm.

Length of Outer Rib [L]:

= Saddle Height - cos( theta/2 )( radius + shlthk + wpdthk ) - bpthk

= 750 - cos( 120/2 )( 462 + 12 + 12 ) - 15

= 491.750 mm.

Intermediate Term [Cc]:

= sqrt( 2 * pi² * Elastic Modulus / Yield Stress )

= sqrt( 2 * pi² * 199943008/207 )

= 138.135

Slenderness ratio [KL/r]:

= KL/r

= 1 * 492/26

= 18.925

Bending Moment [Rm]:

= Fl /( 2 * Bplen ) * e * L / 2

= 37.9/( 2 * 900 ) * 421 * 492/2

= 2.181 Kg-m.

Compressive Allowable, KL/r < Cc( 18.9 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 18.9 )²/(2 * 138² ))207/

( 5/3+3*(18.9 )/(8* 138 )-( 18.9³)/(8*138³)

= 119.3 N./mm²

AISC Unity Check of Outside Ribs ( must be <= 1 )

= Sc/Sca + ( Rm * C1 / I )/Sba

= 2.2/119 +( 2.18 * 70/2744000 )/138

= 0.022

Check of Inside Ribs:

Inertia of Saddle, Inner Ribs - Axial Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib            12.0 |       128.0 |         0.0 |        15.4 |         0.0 |    274.     |

Web           421.3 |        12.0 |         0.0 |        50.6 |         0.0 |    6.07     |

Totals          ... |         ... |         ... |        65.9 |         ... |    280.     |

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/65.9

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Length of Inner Rib [L]:

= Saddle Height - Outside Radius - Bpthk

= 750 - cos( 486/2 )( 15 + 0 + 0 ) - 0

= 248.500 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 280/65.9 )

= 20.621 mm.

Slenderness ratio [KL/r]:

= KL/r

= 1 * 248/20.6

= 12.051

Unit Force [Force,u]:

= Fl / ( 2 * Baseplate Length )

= 37.9/( 2 * 900 )

= 0.021 Kgf/mm.

Moment at base of inner Rib [Mbase,c]:

= Unit Force * e * L

= 0.021 * 421 * 248

= 2.204 Kg-m.

Bending Stress due to Transverse Force and Weight Load [SigmaB,base,c]:

= Bending Moment / Section Modulus

= 2.2/40042

= 0.540 N./mm²

Compressive Allowable, KL/r < Cc( 12.1 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 12.1 )²/(2 * 138² ))207/

( 5/3+3*(12.1 )/(8* 138 )-( 12.1³)/(8*138³)

= 121.3 N./mm²

AISC Unity Check of Inside Ribs ( must be <= 1 )

= Sc/Sca + ( Mbase,c * C1/I )/Sba

= 2.69/121 +( 2.2 * 70/280 )/138

= 0.026

Warning: bolt dia. 20.000 not found in database, using 19.050 mm.

Input Data for Base Plate Bolting Calculations:

Total Number of Bolts per BasePlate            Nbolts           4

Total Number of Bolts in Tension/Baseplate        Nbt           2

Bolt Material Specification                             SA-193 B7

Bolt Allowable Stress                            Stba      283.00  N./mm²

Bolt Corrosion Allowance                          Bca         0.0  mm.

Distance from Bolts to Edge                   Edgedis       120.0  mm.

Nominal Bolt Diameter                             Bnd     19.0500  mm.

Thread Series                                  Series          TEMA

BasePlate Allowable Stress                          S      108.25  N./mm²

Area Available in a Single Bolt               BltArea      1.9484  cm²

Saddle Load QO (Weight)                            QO      3790.2  Kgf

Saddle Load QL (Wind/Seismic contribution)         QL        20.0  Kgf

Maximum Transverse Force                           Ft        78.7  Kgf

Maximum Longitudinal Force                         Fl        37.9  Kgf

Saddle Bolted to Steel Foundation                          No

Shear Stress in a Single Bolt, Longitudinal Direction [taub,l]:

= Fl / ( Bolt Area * Number of Bolts )

= 37.9/( 1.95 * 4 )

= 0.5 N./mm².  Must be less than 146.2 N./mm².

Shear Stress in a Single Bolt, Transverse Direction [taub,t]:

= Ft / ( Bolt Area * Number of Bolts )

= 78.7/( 1.95 * 4 )

= 1.0 N./mm².  Must be less than 146.2 N./mm².

Bolt Area Calculation per Dennis R. Moss

Bolt Area Requirement Due to Longitudinal Load [Bltarearl]:

= 0.0 (QO > QL --> No Uplift in Longitudinal direction)

Bolt Area due to Shear Load [Bltarears]:

= Fl / ( BoltShearAllowable * Nbolts )

= 37.9/(146 * 4 )

= 0.0064 cm²

Bolt Area due to Transverse Load:

Moment on Baseplate Due to Transverse Load [Rmom]:

= B * Ft + Sum of X Moments

= 750 * 78.7 + 0

= 59.04 Kg-m.

Eccentricity (e):

= Rmom / QO

= 59/3790

= 15.58 mm. < Bplen/6 --> No Uplift in Transverse direction

Bolt Area due to Transverse Load [Bltareart]:

= 0 (No Uplift)

Required Area of a Single Bolt [Bltarear]:

= max[Bltarearl, Bltarears, Bltareart]

= max[0, 0.0064, 0 ]

= 0.0064 cm²

ASME VIII Division 2 Horizontal Vessel Analysis, Right Saddle:

Input and Calculated Values:

Vessel Mean Radius                            Rm      470.00  mm.

Shell Thickness used in this Case              t      12.000  mm.

Stiffened Vessel Length per 4.15.6             L     3050.00  mm.

Distance from Saddle to Vessel tangent   a1 or a      600.00  mm.

Saddle Width                             b1 or b      140.00  mm.

Saddle Bearing Angle              delta or theta      120.00  degrees

Wear Plate Width                        b2 or b1      300.00  mm.

Wear Plate Bearing Angle        delta2 or theta1      132.00  degrees

Wear Plate Thickness                    e2 or tr        12.0  mm.

Wear Plate Allowable Stress             fw or Sr      137.90  N./mm²

Inside Depth of Head                    Hi or h2      234.25  mm.

Shell Allowable Stress used in Calculation            235.81  N./mm²

Head Allowable Stress used in Calculation             235.81  N./mm²

Circumferential Efficiency in Plane of Saddle           1.00

Circumferential Efficiency at Mid-Span                  1.00

Distance from Saddle Base to Centerline        B      750.00  mm.

Coefficient of Friction                       mu        0.30

Saddle Force Q, Test Case, no Ext. Forces            1197.24  Kgf

Pressure used in Analysis                      P      28.646  bars

Horizontal Vessel Analysis Results:      Actual |    Allowable |

N./mm² |       N./mm² |

----------------------------------------------------------------

Long. Stress at Top    of Midspan         74.58 |       235.81 |

Long. Stress at Bottom of Midspan         75.02 |       235.81 |

Long. Stress at Top    of Saddles         77.24 |       235.81 |

Long. Stress at Bottom of Saddles         73.45 |       235.81 |

----------------------------------------------------------------

Tangential Shear in Shell                  1.79 |       139.65 |

Circ. Stress at Horn of Saddle             3.18 |       353.71 |

Circ. Compressive Stress in Shell          0.18 |       235.81 |

----------------------------------------------------------------

Intermediate Results: Saddle Reaction Q due to Wind or Seismic:

Saddle Reaction Force due to Wind Ft  [Fwt]:

= Ftr( Ft/Num of Saddles + Z Force Load ) * B / E

= 3( 157/2 + 0 ) * 750/843

= 210.2 Kgf

Saddle Reaction Force due to Wind Fl  [Fwl]:

= max( Fl, Sum of X Forces) * B / Ls

= max( 37.9, 0 ) * 750/1420

= 20.0 Kgf

Load Combination Results for Q + Wind or Seismic [Q]:

= Saddle Load + max( Fwl, Fwt, Fsl, Fst )

= 987 + max( 20, 210, 0, 0 )

= 1197.2 Kgf

Longitudinal Wind Force [Fl]:

= WindScalar * WindPress( Platform Area + ( End Area * WindDiaMult ) )

= 1 * 1046( 0 +( 0.9 * 1.2 ))

= 1126.093 N

Summary of Loads at the base of this Saddle:

Vertical Load (including saddle weight)              1302.87  Kgf

Transverse Shear Load Saddle           Ft              78.72  Kgf

Longitudinal Shear Load Saddle                         37.89  Kgf

Formulas and Substitutions for Horizontal Vessel Analysis:

Note: Wear Plate is Welded to the Shell, k = 0.1

Saddle Dimension [E]:

= min( 2( ShellID/2 + t + WearPadThickness )sin( theta/2 ), 2*Rm )

= min( 2( 925/2 + 12 + 12 )sin( 120/2 ), 2*470 )

= 842.643 mm.

The Computed K values from Table 4.15.1:

K1  = 0.1066     K2  = 1.1707     K3  = 0.8799     K4  = 0.4011

K5  = 0.7603     K6  = 0.0529     K7  = 0.0529     K8  = 0.3405

K9  = 0.2711     K10 = 0.0581     K1* = 0.1923     K6p = 0.0434

K7p = 0.0434

The suffix 'p' denotes the values for a wear plate if it exists.

Note: Dimension a is greater than or equal to Rm/2.

Moment per Equation 4.15.3 [M1]:

= -Q*a [1 - (1- a/L + (Rm²-h2²)/(2a*L))/(1+(4h2)/3L)]

= -1197*600[1-(1-600/3050+(470²-234²)/

(2*600*3050))/(1+(4*234)/(3*3050))]

= -165.4 Kg-m.

Moment per Equation 4.15.4 [M2]:

= Q*L/4(1+2(Rm²-h2²)/(L²))/(1+(4h2)/( 3L))-4a/L

= 1197*3050/4(1+2(470²-234²)/(3050²))/(1+(4*234)/

(3*3050))-4*600/3050

= 139.3 Kg-m.

Longitudinal Stress at Top of Shell (4.15.6)    [Sigma1]:

= P * Rm/(2t) - M2/(pi*Rm²t)

= 28.6 * 470/(2*9 ) - 139/(pi*470²*9 )

= 74.58 N./mm²

Longitudinal Stress at Bottom of Shell (4.15.7)    [Sigma2]:

= P * Rm/(2t) + M2/(pi * Rm² * t)

= 28.6 * 470/(2 * 9 ) + 139/(pi * 470² * 9 )

= 75.02 N./mm²

Longitudinal Stress at Top of Shell at Support (4.15.10)    [Sigma*3]:

= P * Rm/(2t) - M1/(K1*pi*Rm²t)

= 28.6*470/(2*9)--165/(0.11*pi*470²*9)

= 77.24 N./mm²

Longitudinal Stress at Bottom of Shell at Support (4.15.11)    [Sigma*4]:

= P * Rm/(2t) + M1/(K1* * pi * Rm² * t)

= 28.6*470/(2*9)+-165/(0.19*pi*470²*9)

= 73.45 N./mm²

Maximum Shear Force in the Saddle (4.15.5)   [T]:

= Q(L-2a)/(L+(4*h2/3))

= 1197( 3050 - 2 * 600 )/(3050 +( 4 * 234/3))

= 658.7 Kgf

Shear Stress in the shell no rings,  not stiffened (4.15.14)   [tau2]:

= K2 * T / ( Rm * t )

= 1.17 * 659/( 470 * 9 )

= 1.79 N./mm²

Decay Length (4.15.22)   [x1,x2]:

= 0.78 * sqrt( Rm * t )

= 0.78 * sqrt( 470 * 9 )

= 50.730 mm.

Effective reinforcing plate width  (4.15.1)   [B1]:

= min( b + 1.56 * sqrt( Rm * t ), 2a  )

= min( 140 + 1.56 * sqrt( 470 * 9 ), 2 * 600 )

= 241.46 mm.

Wear Plate/Shell Stress ratio  (4.15.29)   [eta]:

= 1.0000 Materials are the same, test case

Circumferential Stress at Saddle Base with Wear Plate (4.15.26)   [sigma6,r]:

= -K5 * Q * k / ( B1( t + eta * tr ) )

= -0.76 * 1197 * 0.1/( 241( 9 + 1 * 12 ) )

= -0.18 N./mm²

Circ. Comp. Stress at Horn of Saddle, L<8Rm  (4.15.28)   [sigma7,r*]:

= -Q/(4(t+eta*tr)b1) - 12*K7*Q*Rm/(L(t+eta*tr)²)

= -1197/(4(9 + 1 * 12 )241 ) -

12*0.053*1197*470/(3050(9+1*12)²)

= -3.18 N./mm²

Results for Vessel Ribs, Web and Base:

Baseplate Length                        Bplen          900.0000  mm.

Baseplate Thickness                     Bpthk           15.0000  mm.

Baseplate Width                         Bpwid          170.0000  mm.

Number of Ribs ( inc. outside ribs )    Nribs                 3

Rib Thickness                           Ribtk           12.0000  mm.

Web Thickness                           Webtk           12.0000  mm.

Web Location                           Webloc            Center

Saddle Yield Stress                        Sy             206.9  N./

Height of Web at Center                  Hw,c             367.5  mm.

Friction Coefficient                       mu             0.300

Note: In the tables below Io is I for the rectangle + Area * Centroid Distance^2

Moment of Inertia of Saddle - Transverse Direction (90 degrees to long axis)

B |           D |           Y |           A |          AY |          Io |

----------------------------------------------------------------------------------------------

Shell            401.0 |         9.0 |         4.5 |        36.1 |     16239.4 |   0.295E+04 |

Wearplate        300.0 |        12.0 |        15.0 |        36.0 |     54000.0 |   0.231E+04 |

Web               12.0 |       248.5 |       145.2 |        29.8 |    433135.5 |   0.229E+04 |

BasePlate        170.0 |        15.0 |       277.0 |        25.5 |    706350.0 |   0.846E+04 |

Totals             ... |         ... |         ... |       127.4 |   1209724.9 |   0.160E+05 |

Distance to Centroid [C1]:

= AY / A

= 476/127

= 94.949 mm.

Angle [beta]:

= 180 - Saddle Angle/2

= 180 - 120/2

= 120.0

Saddle Splitting Coefficient [K1]:

= ( 1 + cos(beta) - 0.5*sin(beta)² )/(pi - beta + sin(beta)cos(beta) )

= ( 1 + cos(120 ) - 0.5*sin(120 )² )/(pi - 2.09 + sin(120 )cos(120 ) )

= 0.2035

Saddle Splitting Force [Fh]:

= K1 * Q

= 0.2 * 1197

= 243.6649 Kgf

Tension Stress, St = ( Fh/As )       =          0.2617  N./mm²

Allowed Stress, Sa = 0.6 * Yield Str =        124.1100  N./mm²

Saddle Splitting Dimension [d]:

= B - R * sin(theta/2)/(theta/2 in radians)

= 750 - 466 * sin(120/2)/1.05

= 365.035 mm.

Bending Moment, M  = Fh * d          =         88.9479  Kg-m.

Bending Stress, Sb = ( M * C1 / I  ) =          0.5175  N./mm²

Allowed Stress, Sa = 2/3 * Yield Str =        137.9000  N./mm²

Minimum Thickness of Baseplate per Moss:

= ( 3( Q + Saddle_Wt )BasePlateWidth / ( 4 * BasePlateLength * AllStress ))½

= ( 3(1197 + 106 )170/( 4 * 900 * 138 ))½

= 3.623 mm.

Calculation of Axial Load, Intermediate Values and Compressive Stress:

Web Length Dimension [ Web Length ]:

= 2 * cos( 90 - Saddle Angle/2 )( Inside Radius + Shell Thk + Wear Plate Thk )

= 2 * cos( 90 - 120/2 )( 462 + 12 + 12 )

= 842.643 mm.

Distance between Ribs [e]:

= Web Length / ( Nribs - 1 )

= 843/( 3 - 1 )

= 421.321 mm.

Baseplate Pressure Area [Ap]:

= e * Bpwid / 2

= 421 * 170/2

= 358.123 cm²

Bearing Pressure [Bp]:

= Q / ( BasePlateLength * BasePlateWidth )

= 1197/( 900 * 170 )

= 0.783 Kgf/cm²

Axial Load [P]:

= Ap * Bp

= 358 * 0.78

= 280.236 Kgf

Area of the Rib and Web [Ar]:

= Rib Area + Web Area

= 15.4 + 25.3

= 40.639 cm²

Compressive Stress [Sc]:

= P/Ar

= 280/40.6

= 0.676 N./mm²

Check of Outside Ribs:

Inertia of Saddle, Outer Ribs - Longitudinal Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib+Web        12.0 |       140.0 |         ... |        16.8 |         ... |    274.     |

Rib dimension [D]:

= Saddle Width - Web Thickness

= 140 - 12

= 128.000 mm.

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/40.6

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 274/40.6 )

= 25.985 mm.

Length of Outer Rib [L]:

= Saddle Height - cos( theta/2 )( radius + shlthk + wpdthk ) - bpthk

= 750 - cos( 120/2 )( 462 + 12 + 12 ) - 15

= 491.750 mm.

Intermediate Term [Cc]:

= sqrt( 2 * pi² * Elastic Modulus / Yield Stress )

= sqrt( 2 * pi² * 199943008/207 )

= 138.135

Slenderness ratio [KL/r]:

= KL/r

= 1 * 492/26

= 18.925

Bending Moment [Rm]:

= Fl /( 2 * Bplen ) * e * L / 2

= 37.9/( 2 * 900 ) * 421 * 492/2

= 2.181 Kg-m.

Compressive Allowable, KL/r < Cc( 18.9 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 18.9 )²/(2 * 138² ))207/

( 5/3+3*(18.9 )/(8* 138 )-( 18.9³)/(8*138³)

= 119.3 N./mm²

AISC Unity Check of Outside Ribs ( must be <= 1 )

= Sc/Sca + ( Rm * C1 / I )/Sba

= 0.68/119 +( 2.18 * 70/2744000 )/138

= 0.010

Check of Inside Ribs:

Inertia of Saddle, Inner Ribs - Axial Direction

B |           D |           Y |           A |          AY |          Io |

-------------------------------------------------------------------------------------------

Rib            12.0 |       128.0 |         0.0 |        15.4 |         0.0 |    274.     |

Web           421.3 |        12.0 |         0.0 |        50.6 |         0.0 |    6.07     |

Totals          ... |         ... |         ... |        65.9 |         ... |    280.     |

Distance to Centroid from Datum [ytot]:

= AY / A

= 0/65.9

= 0.000 mm.

Distance to Centroid [C1]:

= Saddle Width / 2

= 140/2

= 70.000 mm.

Length of Inner Rib [L]:

= Saddle Height - Outside Radius - Bpthk

= 750 - cos( 486/2 )( 15 + 0 + 0 ) - 0

= 248.500 mm.

Radius of Gyration [r]:

= sqrt( Total Inertia / Total Area )

= sqrt( 280/65.9 )

= 20.621 mm.

Slenderness ratio [KL/r]:

= KL/r

= 1 * 248/20.6

= 12.051

Unit Force [Force,u]:

= Fl / ( 2 * Baseplate Length )

= 37.9/( 2 * 900 )

= 0.021 Kgf/mm.

Moment at base of inner Rib [Mbase,c]:

= Unit Force * e * L

= 0.021 * 421 * 248

= 2.204 Kg-m.

Bending Stress due to Transverse Force and Weight Load [SigmaB,base,c]:

= Bending Moment / Section Modulus

= 2.2/40042

= 0.540 N./mm²

Compressive Allowable, KL/r < Cc( 12.1 < 138 ) per AISC E2-1 [Sca]:

= ( 1-(Klr)²/(2*Cc²))Fy/(5/3+3*(Klr)/(8*Cc)-(Klr³)/(8*Cc³)

= ( 1-( 12.1 )²/(2 * 138² ))207/

( 5/3+3*(12.1 )/(8* 138 )-( 12.1³)/(8*138³)

= 121.3 N./mm²

AISC Unity Check of Inside Ribs ( must be <= 1 )

= Sc/Sca + ( Mbase,c * C1/I )/Sba

= 0.83/121 +( 2.2 * 70/280 )/138

= 0.011

Warning: bolt dia. 20.000 not found in database, using 19.050 mm.

Input Data for Base Plate Bolting Calculations:

Total Number of Bolts per BasePlate            Nbolts           4

Total Number of Bolts in Tension/Baseplate        Nbt           2

Bolt Material Specification                             SA-193 B7

Bolt Allowable Stress                            Stba      283.00  N./mm²

Bolt Corrosion Allowance                          Bca         0.0  mm.

Distance from Bolts to Edge                   Edgedis       120.0  mm.

Nominal Bolt Diameter                             Bnd     19.0500  mm.

Thread Series                                  Series          TEMA

BasePlate Allowable Stress                          S      108.25  N./mm²

Area Available in a Single Bolt               BltArea      1.9484  cm²

Saddle Load QO (Weight)                            QO      1092.7  Kgf

Saddle Load QL (Wind/Seismic contribution)         QL        20.0  Kgf

Maximum Transverse Force                           Ft        78.7  Kgf

Maximum Longitudinal Force                         Fl        37.9  Kgf

Saddle Bolted to Steel Foundation                          No

Shear Stress in a Single Bolt, Longitudinal Direction [taub,l]:

= Fl / ( Bolt Area * Number of Bolts )

= 37.9/( 1.95 * 4 )

= 0.5 N./mm².  Must be less than 146.2 N./mm².

Shear Stress in a Single Bolt, Transverse Direction [taub,t]:

= Ft / ( Bolt Area * Number of Bolts )

= 78.7/( 1.95 * 4 )

= 1.0 N./mm².  Must be less than 146.2 N./mm².

Bolt Area Calculation per Dennis R. Moss

Bolt Area Requirement Due to Longitudinal Load [Bltarearl]:

= 0.0 (QO > QL --> No Uplift in Longitudinal direction)

Bolt Area due to Shear Load [Bltarears]:

= Fl / ( BoltShearAllowable * Nbolts )

= 37.9/(146 * 4 )

= 0.0064 cm²

Bolt Area due to Transverse Load:

Moment on Baseplate Due to Transverse Load [Rmom]:

= B * Ft + Sum of X Moments

= 750 * 78.7 + 0

= 59.04 Kg-m.

Eccentricity (e):

= Rmom / QO

= 59/1093

= 54.04 mm. < Bplen/6 --> No Uplift in Transverse direction

Bolt Area due to Transverse Load [Bltareart]:

= 0 (No Uplift)

Required Area of a Single Bolt [Bltarear]:

= max[Bltarearl, Bltarears, Bltareart]

= max[0, 0.0064, 0 ]

= 0.0064 cm²

Warning:

Please note that nozzle loadings, if included, are assumed to be local in nature

and will not contribute to or create a net section bending moment.  Therefore, the

addition of nozzle loads will not affect the support load calculation.  If you wish

to create a load on the legs/lugs etc. from forces or moments, use the Force/Moment dialog

and add the appropriate forces and moments at the correct locations in the model. Ensure

that all supports are designed to take into account all possible loading conditions.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Conical Reinforcement Calculations, ASME VIII Div. 1, App. 1

Input Values:

SH. Cone

Design Internal Pressure, Small End                   22.048  bars

Design Internal Pressure, Large End                   22.048  bars

Temperature for Internal Pressure                      120.0  °C

Design External Pressure                               1.034  bars

Temperature for External Pressure                      120.0  °C

Cone Material                                      SA-516 70

Cone Allowable Stress at Temperature          Ss      137.90  N./mm²

Cone Allowable Stress At Ambient                      137.90  N./mm²

Longitudinal Joint Efficiency of Cone                   1.00

Circumferential Joint Efficiency of Cone                1.00

Actual Thickness of Cone                      Tc     12.0000  mm.

Corrosion Allowance for Cone                 Cac      3.0000  mm.

Diameter Basis for Cone and Cylinders                     ID

Diameter of Small End of Cone                 Ds     600.000  mm.

Diameter of Large End of Cone                 Dl     925.000  mm.

Half Apex Angle for Cone                               30.00  degrees

Axial Length of Cone                          Lc     565.000  mm.

Small End Cylinder Material                        SA-516 70

Small Cylinder Allowable Stress at Operating  Ss      137.90  N./mm²

Small Cylinder Allowable Stress At Ambient            137.90  N./mm²

Joint Efficiency of Small Cylinder            Es      1.0000

Actual Thickness of Small Cylinder            Ts     12.0000  mm.

Corrosion Allowance for Small Cylinder       Cas      3.0000  mm.

Axial Length of Small Cylinder                Ls     150.000  mm.

Large End Cylinder Material                        SA-516 70

Large Cylinder Allowable Stress at Operating  Sl      137.90  N./mm²

Large Cylinder Allowable Stress At Ambient            137.90  N./mm²

Joint Efficiency of Large Cylinder            El      1.0000

Actual Thickness of Large Cylinder            Tl     12.0000  mm.

Corrosion Allowance for Large Cylinder       Cal      3.0000  mm.

Axial Length of Large Cylinder                Ll    2892.083  mm.

Type of Reinforcement at Large End of Cone:             None

Large End Reinforcing/Knuckle Material

Large Reinforcing/Knuckle Allowable, Operating        137.90  N./mm²

Large Reinforcing/Knuckle Allowable, Ambient          137.90  N./mm²

Type of Reinforcement at Small End of Cone:             None

Small End Reinforcing/Knuckle Material

Small Reinforcing/Knuckle Allowable, Operating        137.90  N./mm²

Small Reinforcing/Knuckle Allowable, Ambient          137.90  N./mm²

Calculated Values:

Elastic Modulus Data from ASME Section II Part D at 120 °C

Elastic Modulus of Cone Material                 0.197E+09 KPa. at 119 °C

Elastic Modulus of Small Cylinder Material       0.197E+09 KPa. at 119 °C

Elastic Modulus of Large Cylinder Material       0.197E+09 KPa. at 119 °C

Elastic Modulus of Large End Reinforcement       0.197E+09 KPa. at 119 °C

Elastic Modulus of Small End Reinforcement       0.197E+09 KPa. at 119 °C

Elastic Modulus Data from ASME Section II Part D at 120 °C

Elastic Modulus of Cone Material                 0.197E+09 KPa. at 119 °C

Elastic Modulus of Small Cylinder Material       0.197E+09 KPa. at 119 °C

Elastic Modulus of Large Cylinder Material       0.197E+09 KPa. at 119 °C

Elastic Modulus of Large End Reinforcement       0.197E+09 KPa. at 119 °C

Elastic Modulus of Small End Reinforcement       0.197E+09 KPa. at 119 °C

Axial forces and moments are not computed for Horizontal geometries.

Compute them manually and enter the loads using the Force/Moment dialog.

Place the loads at the ends of the cone as needed.

Note: Small end of the Cone is taken as a Line of Support

Maximum Centroid Reinforcement Distance Large End    16.3373  mm.

Maximum Centroid Reinforcement Distance Small End    13.2476  mm.

Note: No ring was found close enough to the large end to be considered.

Note: No ring was found close enough to the small end to be considered.

Reinforcement Calculations for Cone / Large Cylinder:

Required Area of Reinforcement for Large End Under Internal Pressure

Large end ratio of pressure to allowable stress    P/Ss E1    0.01599

Large end max. half apex angle w/o reinforcement     delta     30.000  degrees

Large end actual half apex angle                     alpha     30.000  degrees

Intermediate Value [k]:

= max( Y / ( Sr * Erl ), 1 )

= max( 27.15E+09/( 138 * 196910448 ), 1 )

= 1.0000

where [Y] is:

= Large End All. Stress * Large End Elastic Modulus (Int. temp.)

= 138 * 196910448

= 27153948672.0 N./mm²^2

Decay Length, Cone Large End:

= 2 * sqrt( RL( ts - ca ) )

= 2 * sqrt( 466( 12 - 3 ) )

= 129.453 mm.

Required Area of Reinforcement, Large End, Internal [Arl]:

= k*QL*Rl/(Ss*E1))*(1-delta/alpha)*tan(alpha)

= 1 * 52.3 * 466/( 138 * 1 ) *( 1 - 30/30 ) * 0.58

= 0 cm²

Force per Length, Cone Large End [QL]:

= P( Rl/2 ) + f1

= 22( 466/2 ) + 0

= 52.332 Kgf/mm.

Axial Load per Unit Circumference excluding Pressure [f1]:

= Faxial/(pi(Ds + Ts)) + Moment/(pi(Rs + Ts/2)(Rs + Ts/2))

= -0/(pi(931+12))+0/(pi(466+12/2)(466+12/2))

= 0.0 Kgf/mm.

Area of Reinforcement Available in Large end Shell [Ael]:

= (Ts-t)*sqrt(Rl*Ts)+(Tc-Tr)*sqrt(Rl*Tc/cos(alpha))

= ( 9 - 7.52 ) * SQRT( 466 * 9 ) +

( 9 - 8.68 ) * SQRT( 466 * 9/0.87 )

= 1.1850 cm²

Summary of Reinforcement area, Large end, Internal Pressure:

Area of reinforcement required per App. 1-5(1)        0.0000  cm²

Area of reinforcement in shell per App. 1-5(2)        1.1850  cm²

Area of reinforcement in stiffening ring              0.0000  cm²

Required Area of Reinforcement for Large End Under External Pressure

Large end ratio of pressure to allowable stress    P/Ss E1    0.00075

Large end max. half apex angle w/o reinforcement     delta      1.875  degrees

Large end actual half apex angle                     alpha     30.000  degrees

Intermediate Value [k]:

= max( Y / ( Srl * Erl ), 1 )

= max( 27.15E+09/( 138 * 196910448 ), 1 )

= 1.0000

where [Y] is:

= Large End All. Stress * Large End Elastic Modulus (Ext. temp.)

= 138 * 196910448

= 27153948672.0 N./mm²^2

Allowable Stress of Large End Material (Ext. Temp)   137.9  N./mm²

Allowable Stress of Cone Material (Ext. Temp)        137.9  N./mm²

Required Area of Reinforcement, Large End, External [Arl]:

= (k*QL*Rl*tan(angle)/(Ss*E1))*(1-1/4((P*Rl-QL)/QL)*(delta/alpha)

= (1*2.5*474*0.58/(138*1))*

(1-1/4((1.03*474-2.5)/2.5)*(1.88/30)

= 0.48 cm²

Force per Length, Cone Large End External Pressure [QL]:

= Pext( Rl/2 ) + f1

= 1.03( 474/2 ) + 0

= 2.502 Kgf/mm.

Axial Load per Unit Circumference excluding Pressure [f1]:

= Faxial/(pi(Ds + Ts)) + Moment/(pi(Rs + Ts/2)(Rs + Ts/2))

= +0/(pi(949-12))+0/(pi(474-12/2)(474-12/2))

= 0.0 Kgf/mm.

Available Area of Reinforcement, Large End, External [Ael]:

= 0.55*( Dl*ts )½ * ( ts + tc/cos(alpha) )

= 0.55 *( 949 * 9 )½ *( 9 + 9/0.87 )

= 9.8570 cm²

Summary of Reinforcement Area, Large End, External Pressure:

Area of reinforcement required per App. 1-8(1)        0.4798  cm²

Area of reinforcement in shell per App. 1-8(2)        9.8570  cm²

Area of reinforcement in stiffening ring              0.0000  cm²

Reinforcement Calculations for Cone / Small Cylinder:

Required Area of Reinforcement for Small End under Internal Pressure

Small end ratio of pressure to allowable stress    P/Ss E1    0.01599

Small end max. half apex angle w/o reinforcement     delta     11.096  degrees

Small end actual half apex angle                     alpha     30.000  degrees

Intermediate Value [k]:

= max( Y / ( Sr * Ers ), 1 )

= max( 27.15E+09/( 138 * 196910448 ), 1 )

= 1.0000

where [Y] is:

= Small End All. Stress * Small End Elastic Modulus (Int. temp.)

= 138 * 196910448

= 27153948672.0 N./mm²^2

Decay Length, Cone Small End:

= 1.4 * sqrt( Rs( ts - ca ) )

= 1.4 * sqrt( 303( 12 - 3 ) )

= 73.109 mm.

Required Area of Reinforcement, Small End, Internal [Ars]:

= k*QS*Rs/(Ss*E1)*(1-delta/alpha)*tan(alpha)

= 1 * 34.1 * 303/( 138 * 1 ) *( 1 - 11.1/30 )0.58

= 2.67 cm²

Force per Length, Cone Small End [QS]:

= P( Rs/2 ) + f2

= 22( 303/2 ) + 0

= 34.063 Kgf/mm.

Axial Load per Unit Circumference excluding Pressure [f2]:

= Faxial/(pi(Ds + Ts)) + Moment/(pi(Rs + Ts/2)(Rs + Ts/2))

= -0/(pi(606+12))+0/(pi(303+12/2)(303+12/2))

= 0.0 Kgf/mm.

Area of Reinforcement Available in Small End Shell [Aes]:

= 0.78(Rs*Ts)½*((Ts-t)+(Tc-Tr)/cos(alpha) ))

= 0.78(303 *9 )½*(( 9 -4.89 )+( 9 -5.65 )/0.87 )

= 3.2496 cm²

Summary of Reinforcement Area, Small End, Internal Pressure:

Area of reinforcement required per App. 1-5(3)        2.6703  cm²

Area of reinforcement in shell per App. 1-5(4)        3.2496  cm²

Area of reinforcement in stiffening ring              0.0000  cm²

Required Area of Reinforcement for Small End Under External Pressure

Allowable Stress of Small End Material (Ext. Temp)    137.9  N./mm²

Allowable Stress of Cone Material (Ext. Temp)         137.9  N./mm²

Intermediate Value [k]:

= max( Y / ( Srs * Ers ), 1 )

= max( 27.15E+09/( 138 * 196910448 ), 1 )

= 1.0000

where [Y] is:

= Small End All. Stress * Small End Elastic Modulus (Ext. temp.)

= 138 * 196910448

= 27153948672.0 N./mm²^2

Area of Reinforcement Required in Small End Shell [Ars]:

= k * QS * Rs * tan(alpha) / ( Ss * E1 )

= (1*1.65*312*0.58/(138*1))

= 0.211 cm²

Force per Length, Cone Small End [QS]:

= Pext( Rs/2 ) + f2

= 1.03( 312/2 ) + 0

= 1.645 Kgf/mm.

Axial Load per Unit Circumference excluding Pressure [f2]:

= Faxial/(pi(Ds + Ts)) + Moment/(pi(Rs + Ts/2)(Rs + Ts/2))

= +0/(pi(624-12))+0/(pi(312-12/2)(312-12/2))

= 0.0 Kgf/mm.

Area of Reinforcement Available in Small End Shell [Aes]:

= 0.55*(Ds*ts)½*[(ts-t)+(tc-tr)/cos(alpha))]

= 0.55*(624*9)½*[(9-1.1)+(9-2.05)/0.87]

= 6.5630 cm²

Summary of Reinforcement Area, Small End, External Pressure:

Area of reinforcement required per App. 1-8(3)        0.2108  cm²

Area of reinforcement in shell per App. 1-8(4)        6.5630  cm²

Area of reinforcement in stiffening ring              0.0000  cm²

Intermediate Results, Small End, External Pressure:

Area Available in Cone, Shell, and Reinforcement       33.21  cm²

Force per Unit Length on Shell / Cone Junction          2.99  Kgf/mm.

Actual Buckling Stress associated with this Force       4.13  N./mm²

Material Strain associated with this stress         0.000042

Required Moment of Inertia, Small End, External Pressure [I's]:

= A * Ds² * Ats / 10.9

= 0.41944E-04 * 624 * 624 * 33.2/10.9

= 4975.36 mm.4

Available Moment of Inertia, Small End, External Pressure:

Area  Centroid     Ar*Ce           Dist         I    Ar*Di²

Shl      3.710    0.0000     0.000         6.3763     0.250   150.819

Con      4.283   11.8983    50.965        -5.5220     2.407   130.613

Sec      0.000    4.5000     0.000         1.8763     0.000     0.000

TOT      7.993              50.965                    2.657   281.431

---------------------------------------------------------------------

Centroid of Section         6.3763     Moment of Inertia         5.47

Summary of Small End Inertia Calculations

Available Moment of Inertia ( Small End )            0.5472E+01  cm**4

Required  Moment of Inertia ( Small End )            0.4975E+00  cm**4

Note: The following calculations are only required per 1-5(g)(1) and

do include external loads due to wind or seismic.  These

discontinuity stresses are computed at the shell/cone junction

and do not include effects of local stiffening from a junction ring.

Results for Discontinuity Stresses per Bednar p. 236 2nd Edition

Stress Type              Stress      Allowable          Location

Tensile  Stress          180.72          413.70  Small Cyl. Long.

Compres. Stress         -105.38         -413.70  Small Cyl. Long.

Membrane Stress          154.08         -206.85   Small End Tang.

Tensile  Stress          186.54          413.70 Cone Longitudinal

Compres. Stress          -99.55         -413.70 Cone Longitudinal

Compres  Stress          165.73         -206.85   Cone Tangential

Tensile  Stress          327.88          413.70  Large Cyl. Long.

Compres. Stress         -212.74         -413.70  Large Cyl. Long.

Membrane Stress          -33.64         -206.85   Large End Tang.

Tensile  Stress          336.79          413.70 Cone Longitudinal

Compres. Stress         -203.83         -413.70 Cone Longitudinal

Compres  Stress          -15.83         -206.85   Cone Tangential

Note: An asterisk (*) denotes that this stress was not applicable

for this combination of loads.

Maximum Allowable Pressure Calculations for Cone to Shell Junction:

Pressure      Pressure                                                 Reason

Case          bars                           for Failure at this Pressure

-------------------------------------------------------------------------------

MAWP        22.861     Thickness due to internal pressure, Cone Large End

MAPnc        30.576     Thickness due to internal pressure, Cone Large End

These pressures were determined by iteration.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: T1 (3in.)                         From:   20

Pressure for Reinforcement Calculations        P       6.801  bars

Temperature for Internal Pressure           Temp          85  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex          85  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      600.00  mm.

Design Length of Section                       L    400.0000  mm.

Shell Finished (Minimum) Thickness             t     10.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Cylinder/Cone Centerline        L1    100.0000  mm.

Distance from Bottom/Left Tangent                     200.00  mm.

User Entered Minimum Design Metal Temperature         -29.00  °C

Type of Element Connected to the Parent : Nozzle

Material                                            SA-106 B

Material UNS Number                                   K03006

Material Specification/Type                       Smls. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                    Outside

Layout Angle                                          108.82  deg

Diameter                                              3.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                         80

Flange Material                                       SA-105

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    200.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     10.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Pad Material    [Normalized]                       SA-516 70

Pad Allowable Stress at Temperature           Sp      137.90  N./mm²

Pad Allowable Stress At Ambient              Spa      137.90  N./mm²

Diameter of Pad along vessel surface          Dp    190.0000  mm.

Thickness of Pad                              te     10.0000  mm.

Weld leg size between Pad and Shell           Wp      8.0000  mm.

Groove weld depth between Pad and Nozzle    Wgpn     10.0000  mm.

Reinforcing Pad Width                                50.5500  mm.

Flange Class                                             150

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle With Pad, no Inside projection

Note : Checking Nozzle 90 degrees to the Longitudinal axis.

Reinforcement CALCULATION, Description: T1 (3in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            3.500  in.

Actual Thickness Used in Calculation                   0.263  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (6.8*303)/(138*1-0.6*6.8)

= 1.4990 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (6.8*44.5)/(118*1+0.4*6.8)

= 0.2558 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3989  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   173.5622  mm.

Parallel to Vessel Wall, opening length              d    86.7811  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    17.5000  mm.

Note: The Pad diameter is greater than the Diameter Limit. The excess will not be considered.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: T1 (3in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld, min( Curve:B, Curve:A)

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve A              -8 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Min Metal Temp. w/o impact per UG-20(f)                    -29 °C

Nozzle Neck to Pad Weld for the Nozzle, Curve: B

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve B             -29 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Nozzle Neck to Pad Weld for Reinforcement pad, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Shell to Pad Weld Junction at Pad OD, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 10, tr = 1.5, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.21, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), min( Curve:B, Curve:D)

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve B             -29 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the Nozzle                                :  -104 °C

Gov. MDMT of the Reinforcement Pad                     :  -104 °C

Gov. MDMT of the nozzle to shell joint welded assembly :  -104 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

Unadjusted MDMT of ASME B16.5/47 flanges per UCS-66(c)     -18 °C

Flange MDMT with Temp reduction per UCS-66(b)(1)(-b)      -104 °C

Where the Stress Reduction Ratio per UCS-66(b)(1)(-b) is :

Design Pressure/Ambient Rating = 6.80/19.60 = 0.347

Weld Size Calculations, Description: T1 (3in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      3.6675  mm.

Intermediate Calc. for pad/shell Welds   TminPad      7.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          2.5673 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             3.5000 = 0.5*TminPad  5.6560 = 0.7 * Wp mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   16.6  bars

Note : Checking Nozzle in plane parallel to the vessel axis.

Reinforcement CALCULATION, Description: T1 (3in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            3.500  in.

Actual Thickness Used in Calculation                   0.263  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (6.8*303)/(138*1-0.6*6.8)

= 1.4990 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (6.8*44.5)/(118*1+0.4*6.8)

= 0.2558 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3989  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   163.1300  mm.

Parallel to Vessel Wall, opening length              d    81.5650  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    17.5000  mm.

Note: The Pad diameter is greater than the Diameter Limit. The excess will not be considered.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: T1 (3in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.3989 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 4.4990 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 4.5000 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 7.8000 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 7.8, max( 4.5, 4.5 ) ]

= 4.5000 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.4, 4.5 )

= 4.5000 mm.

Available Nozzle Neck Thickness = 6.6675 mm. --> OK

Weld Size Calculations, Description: T1 (3in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      3.6675  mm.

Intermediate Calc. for pad/shell Welds   TminPad      7.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          2.5673 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             3.5000 = 0.5*TminPad  5.6560 = 0.7 * Wp mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   16.6  bars

The Drop for this Nozzle is : 19.9089 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 230.4942 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: T2 (3in.)                         From:   20

Pressure for Reinforcement Calculations        P       6.853  bars

Temperature for Internal Pressure           Temp          85  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex          85  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      600.00  mm.

Design Length of Section                       L    400.0000  mm.

Shell Finished (Minimum) Thickness             t     10.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Cylinder/Cone Centerline        L1    100.0000  mm.

Distance from Bottom/Left Tangent                     200.00  mm.

User Entered Minimum Design Metal Temperature         -29.00  °C

Type of Element Connected to the Parent : Nozzle

Material                                            SA-106 B

Material UNS Number                                   K03006

Material Specification/Type                       Smls. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                    Outside

Layout Angle                                          251.18  deg

Diameter                                              3.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                         80

Flange Material                                       SA-105

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    200.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     10.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Pad Material    [Normalized]                       SA-516 70

Pad Allowable Stress at Temperature           Sp      137.90  N./mm²

Pad Allowable Stress At Ambient              Spa      137.90  N./mm²

Diameter of Pad along vessel surface          Dp    190.0000  mm.

Thickness of Pad                              te     10.0000  mm.

Weld leg size between Pad and Shell           Wp      8.0000  mm.

Groove weld depth between Pad and Nozzle    Wgpn     10.0000  mm.

Reinforcing Pad Width                                50.5500  mm.

Flange Class                                             150

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle With Pad, no Inside projection

Note : Checking Nozzle 90 degrees to the Longitudinal axis.

Reinforcement CALCULATION, Description: T2 (3in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            3.500  in.

Actual Thickness Used in Calculation                   0.263  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (6.85*303)/(138*1-0.6*6.85)

= 1.5103 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (6.85*44.5)/(118*1+0.4*6.85)

= 0.2578 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3989  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   173.5622  mm.

Parallel to Vessel Wall, opening length              d    86.7811  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    17.5000  mm.

Note: The Pad diameter is greater than the Diameter Limit. The excess will not be considered.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: T2 (3in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld, min( Curve:B, Curve:A)

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve A              -8 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Min Metal Temp. w/o impact per UG-20(f)                    -29 °C

Nozzle Neck to Pad Weld for the Nozzle, Curve: B

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve B             -29 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Nozzle Neck to Pad Weld for Reinforcement pad, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Shell to Pad Weld Junction at Pad OD, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 10, tr = 1.51, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.22, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), min( Curve:B, Curve:D)

----------------------------------------------------------------------

Govrn. thk, tg = 6.67, tr = 0.26, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.07, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve B             -29 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the Nozzle                                :  -104 °C

Gov. MDMT of the Reinforcement Pad                     :  -104 °C

Gov. MDMT of the nozzle to shell joint welded assembly :  -104 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

Unadjusted MDMT of ASME B16.5/47 flanges per UCS-66(c)     -18 °C

Flange MDMT with Temp reduction per UCS-66(b)(1)(-b)      -104 °C

Where the Stress Reduction Ratio per UCS-66(b)(1)(-b) is :

Design Pressure/Ambient Rating = 6.85/19.60 = 0.350

Weld Size Calculations, Description: T2 (3in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      3.6675  mm.

Intermediate Calc. for pad/shell Welds   TminPad      7.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          2.5673 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             3.5000 = 0.5*TminPad  5.6560 = 0.7 * Wp mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   16.6  bars

Note : Checking Nozzle in plane parallel to the vessel axis.

Reinforcement CALCULATION, Description: T2 (3in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            3.500  in.

Actual Thickness Used in Calculation                   0.263  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (6.85*303)/(138*1-0.6*6.85)

= 1.5103 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (6.85*44.5)/(118*1+0.4*6.85)

= 0.2578 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3989  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   163.1300  mm.

Parallel to Vessel Wall, opening length              d    81.5650  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    17.5000  mm.

Note: The Pad diameter is greater than the Diameter Limit. The excess will not be considered.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: T2 (3in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.3989 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 4.5103 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 4.5103 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 7.8000 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 7.8, max( 4.51, 4.5 ) ]

= 4.5103 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.4, 4.51 )

= 4.5103 mm.

Available Nozzle Neck Thickness = 6.6675 mm. --> OK

Weld Size Calculations, Description: T2 (3in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      3.6675  mm.

Intermediate Calc. for pad/shell Welds   TminPad      7.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          2.5673 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             3.5000 = 0.5*TminPad  5.6560 = 0.7 * Wp mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   16.6  bars

The Drop for this Nozzle is : 19.9089 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 230.4942 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: S1 (4in.)                         From:   60

Pressure for Reinforcement Calculations        P      22.031  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cone at Nozzle Location     D      685.40  mm.

Equivalent Length of Conical Section          Le   2892.0833  mm.

Cone Half Apex Angle                       Alpha       30.00  Degrees

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                     898.52  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                     SA-333 6

Material UNS Number                                   K03006

Material Specification/Type                Smls. & wld. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                    Outside

Layout Angle                                          270.00  deg

Diameter                                              4.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                        120

Flange Material                                   SA-350 LF2

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    180.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Pad Material    [Normalized]                       SA-516 70

Pad Allowable Stress at Temperature           Sp      137.90  N./mm²

Pad Allowable Stress At Ambient              Spa      137.90  N./mm²

Diameter of Pad along vessel surface          Dp    220.0000  mm.

Thickness of Pad                              te     12.0000  mm.

Weld leg size between Pad and Shell           Wp     10.0000  mm.

Groove weld depth between Pad and Nozzle    Wgpn     12.0000  mm.

Reinforcing Pad Width                                52.8500  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle With Pad, no Inside projection

Reinforcement CALCULATION, Description: S1 (4in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            4.500  in.

Actual Thickness Used in Calculation                   0.383  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Conical Transition, Tr [Int. Press]

= (P*D)/(2*cos(a)*(Sv*E-0.6*P)) Appendix 1-4(e)

= (22*(692+2*0))/   (2*0.87*(138*1-0.6*22))

= 6.4481 mm.

Reqd Cone thickness at Nozzle Location under External Pres. :  8.6123  mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (22*57.1)/(118*1+0.4*22)

= 1.0601 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.4431  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   201.6618  mm.

Parallel to Vessel Wall, opening length              d   100.8309  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    22.5000  mm.

Note: The Pad diameter is greater than the Diameter Limit. The excess will not be considered.

Weld Strength Reduction Factor [fr1]:

= min( 1, Sn/Sv )

= min( 1, 118/138 )

= 0.855

Weld Strength Reduction Factor [fr2]:

= min( 1, Sn/Sv )

= min( 1, 118/138 )

= 0.855

Weld Strength Reduction Factor [fr4]:

= min( 1, Sp/Sv )

= min( 1, 138/138 )

= 1.000

Weld Strength Reduction Factor [fr3]:

= min( fr2, fr4 )

= min( 0.85, 1 )

= 0.855

Results of Nozzle Reinforcement Area Calculations: (cm²)

AREA AVAILABLE, A1 to A5     |    Design|  External|     Mapnc|

---------------------------------------------------------------

Area Required             Ar |     6.628|     2.884|        NA|

Area in Shell             A1 |     2.523|     3.350|        NA|

Area in Nozzle Wall       A2 |     2.183|     2.421|        NA|

Area in Inward Nozzle     A3 |     0.000|     0.000|        NA|

Area in Welds    A41+A42+A43 |     0.855|     0.855|        NA|

Area in Element           A5 |    10.483|    10.483|        NA|

TOTAL AREA AVAILABLE    Atot |    16.045|    17.109|        NA|

The Internal Pressure Case Governs the Analysis.

Nozzle Angle Used in Area Calculations                 90.00  Degs.

The area available without a pad is Insufficient.

The area available with the given pad is Sufficient.

SELECTION OF POSSIBLE REINFORCING PADS:   Diameter  Thickness

Based on given Pad Thickness:            123.1852    12.0000  mm.

Based on given Pad Diameter:             220.0000     1.2205  mm.

Based on Shell or Nozzle Thickness:      125.2530     9.7345  mm.

Area Required [A]:

= ( d * tr*F + 2 * tn * tr*F * (1-fr1) ) UG-37(c)

= (101*6.45*1+2*6.73*6.45*1*(1-0.85))

= 6.628 cm²

Reinforcement Areas per Figure UG-37.1

Area Available in Shell [A1]:

= d( E1*t - F*tr ) - 2 * tn( E1*t - F*tr ) * ( 1 - fr1 )

= 101( 1 * 9 - 1 * 6.45 ) - 2 * 6.73

( 1 * 9 - 1 * 6.45 ) *( 1 - 0.85 )

= 2.523 cm²

Area Available in Nozzle Wall Projecting Outward [A2]:

= ( 2 * Tlwp ) * ( tn - trn ) * fr2

= ( 2 * 22.5 ) *( 6.73 - 1.06 ) * 0.85

= 2.183 cm²

Area Available in Welds [A41 + A42 + A43]:

= Wo² * fr3 + (Wi-can/0.707)² * fr2 + Wp² * fr4

= 10² * 0.85 +(0 )² * 0.85 + 0² * 1

= 0.855 cm²

Area Available in Element [A5]:

= (min(Dp,DL)-(Nozzle OD))*(min(tp,Tlwp,te)) * fr4

= ( 202 - 114 ) * 12 * 1

= 10.483 cm²

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 4.0601 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 9.4481 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 9.4481 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.2999 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 8.2578 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 8.26, max( 9.45, 4.5 ) ]

= 8.2578 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 4.06, 8.26 )

= 8.2578 mm.

Available Nozzle Neck Thickness = 9.7345 mm. --> OK

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld (Impact tested)         :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle Neck to Pad Weld for the Nozzle (Impact tested) :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle Neck to Pad Weld for Reinforcement pad, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 9.73, tr = 1.06, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.16, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Shell to Pad Weld Junction at Pad OD, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 12, tr = 6.45, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.72, Temp. Reduction = 16 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 9.73, tr = 1.06, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.16, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the Nozzle                                :  -104 °C

Gov. MDMT of the Reinforcement Pad                     :   -48 °C

Gov. MDMT of the nozzle to shell joint welded assembly :   -48 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

MDMT of ASME B16.5/47 flange per Matl. Specification       -46 °C

Flange MDMT with Temp reduction per UCS-66(i)(2)           -89 °C

Where the Stress Reduction Ratio per UCS-66(i)(2) is :

Design Pressure/Ambient Rating = 22.03/51.10 = 0.431

Weld Size Calculations, Description: S1 (4in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      6.7345  mm.

Intermediate Calc. for pad/shell Welds   TminPad      9.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          4.7142 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             4.5000 = 0.5*TminPad  7.0700 = 0.7 * Wp mm.

Weld Strength and Weld Loads per UG-41.1, Sketch (a) or (b)

Weld Load [W]:

= max( 0, (A-A1+2*tn*fr1*(E1*t-tr))Sv)

= max( 0,(6.63 - 2.52 + 2 * 6.73 * 0.85 *

(1 * 9 - 6.45 ) )138 )

= 6184.64 Kgf

Note: F is always set to 1.0 throughout the calculation.

Weld Load [W1]:

= (A2+A5+A4-(Wi-Can/.707)²*fr2)*Sv

= ( 2.18 + 10.5 + 0.85 - 0 * 0.85 ) * 138

= 19013.51 Kgf

Weld Load [W2]:

= (A2 + A3 + A4 + (2 * tn * t * fr1)) * Sv

= ( 2.18 + 0 + 0.85 +( 1.04 ) ) * 138

= 5729.49 Kgf

Weld Load [W3]:

= (A2+A3+A4+A5+(2*tn*t*fr1))*S

= ( 2.18 + 0 + 0.85 + 10.5 +( 1.04 ) ) * 138

= 20470.87 Kgf

Strength of Connection Elements for Failure Path Analysis

Shear, Outward Nozzle Weld [Sonw]:

= (pi/2) * Dlo * Wo * 0.49 * Snw

= ( 3.14/2.0 ) * 114 * 10 * 0.49 * 118

= 10577. Kgf

Shear, Pad Element Weld [Spew]:

= (pi/2) * DP * WP * 0.49 * SEW

= ( 3.14/2.0 ) * 220 * 10 * 0.49 * 138

= 23811. Kgf

Shear, Nozzle Wall [Snw]:

= (pi *( Dlr + Dlo )/4 ) * ( Thk - Can ) * 0.7 * Sn

= (3.14 * 53.8 ) *( 9.73 - 3 ) * 0.7 * 118

= 9576. Kgf

Tension, Pad Groove Weld [Tpgw]:

= ( pi/2) * Dlo * Wgpn * 0.74 * Seg

= (3.14/2 ) * 114 * 12 * 0.74 * 138

= 22419. Kgf

Tension, Shell Groove Weld [Tngw]:

= (pi/2) * Dlo * ( T - cas ) * 0.74 * Sng

= ( 3.14/2.0 ) * 114 *( 12 - 3 ) * 0.74 * 138

= 16814. Kgf

Strength of Failure Paths:

PATH11 = ( SPEW + SNW ) = ( 23811 + 9576 ) = 33387 Kgf

PATH22 = ( Sonw + Tpgw + Tngw + Sinw )

= ( 10577 + 22419 + 16814 + 0 ) = 49810 Kgf

PATH33 = ( Spew + Tngw + Sinw )

= ( 23811 + 16814 + 0 ) = 40625 Kgf

Summary of Failure Path Calculations:

Path 1-1 = 33386 Kgf, must exceed W = 6184 Kgf or W1 = 19013 Kgf

Path 2-2 = 49809 Kgf, must exceed W = 6184 Kgf or W2 = 5729 Kgf

Path 3-3 = 40625 Kgf, must exceed W = 6184 Kgf or W3 = 20470 Kgf

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   22.8  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

Nozzle is O.K. for the External Pressure           1.03  bars

The Drop for this Nozzle is : 4.7989 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 196.7989 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: S2 (6in.)                         From:   70

Pressure for Reinforcement Calculations        P      22.000  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      925.00  mm.

Design Length of Section                       L   2892.0833  mm.

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                    2413.53  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                     SA-333 6

Material UNS Number                                   K03006

Material Specification/Type                Smls. & wld. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                    Outside

Layout Angle                                           90.00  deg

Diameter                                              6.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                         80

Flange Material                                   SA-350 LF2

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    180.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Pad Material    [Normalized]                       SA-516 70

Pad Allowable Stress at Temperature           Sp      137.90  N./mm²

Pad Allowable Stress At Ambient              Spa      137.90  N./mm²

Diameter of Pad along vessel surface          Dp    300.0000  mm.

Thickness of Pad                              te     12.0000  mm.

Weld leg size between Pad and Shell           Wp     10.0000  mm.

Groove weld depth between Pad and Nozzle    Wgpn     12.0000  mm.

Reinforcing Pad Width                                65.8625  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle With Pad, no Inside projection

Reinforcement CALCULATION, Description: S2 (6in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            6.625  in.

Actual Thickness Used in Calculation                   0.378  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.4986 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (22*84.1)/(118*1+0.4*22)

= 1.5584 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.5566  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   310.1452  mm.

Parallel to Vessel Wall, opening length              d   155.0726  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    22.5000  mm.

Weld Strength Reduction Factor [fr1]:

= min( 1, Sn/Sv )

= min( 1, 118/138 )

= 0.855

Weld Strength Reduction Factor [fr2]:

= min( 1, Sn/Sv )

= min( 1, 118/138 )

= 0.855

Weld Strength Reduction Factor [fr4]:

= min( 1, Sp/Sv )

= min( 1, 138/138 )

= 1.000

Weld Strength Reduction Factor [fr3]:

= min( fr2, fr4 )

= min( 0.86, 1 )

= 0.855

Results of Nozzle Reinforcement Area Calculations: (cm²)

AREA AVAILABLE, A1 to A5     |    Design|  External|     Mapnc|

---------------------------------------------------------------

Area Required             Ar |    11.772|     3.806|        NA|

Area in Shell             A1 |     2.300|     6.358|        NA|

Area in Nozzle Wall       A2 |     1.940|     2.326|        NA|

Area in Inward Nozzle     A3 |     0.000|     0.000|        NA|

Area in Welds    A41+A42+A43 |     1.612|     1.612|        NA|

Area in Element           A5 |    15.807|    15.807|        NA|

TOTAL AREA AVAILABLE    Atot |    21.659|    26.103|        NA|

The Internal Pressure Case Governs the Analysis.

Nozzle Angle Used in Area Calculations                 90.00  Degs.

The area available without a pad is Insufficient.

The area available with the given pad is Sufficient.

SELECTION OF POSSIBLE REINFORCING PADS:   Diameter  Thickness

Based on given Pad Thickness:            217.6076    12.0000  mm.

Based on given Pad Diameter:             300.0000     4.4941  mm.

Based on Shell or Nozzle Thickness:      229.9330     9.6012  mm.

Area Required [A]:

= ( d * tr*F + 2 * tn * tr*F * (1-fr1) ) UG-37(c)

= (155*7.5*1+2*6.6*7.5*1*(1-0.86))

= 11.772 cm²

Reinforcement Areas per Figure UG-37.1

Area Available in Shell [A1]:

= d( E1*t - F*tr ) - 2 * tn( E1*t - F*tr ) * ( 1 - fr1 )

= 155( 1 * 9 - 1 * 7.5 ) - 2 * 6.6

( 1 * 9 - 1 * 7.5 ) *( 1 - 0.86 )

= 2.300 cm²

Area Available in Nozzle Wall Projecting Outward [A2]:

= ( 2 * Tlwp ) * ( tn - trn ) * fr2

= ( 2 * 22.5 ) *( 6.6 - 1.56 ) * 0.86

= 1.940 cm²

Area Available in Welds [A41 + A42 + A43]:

= (Wo² - Ar Lost)*Fr3+((Wi-can/0.707)² - Ar Lost)*fr2 + Trapfr4

= (1 ) * 0.86 +(0 ) * 0.86 + 75.7² * 1

= 1.612 cm²

Area Available in Element [A5]:

= (min(Dp,DL)-(Nozzle OD))*(min(tp,Tlwp,te)) * fr4

= ( 300 - 168 ) * 12 * 1

= 15.807 cm²

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 4.5584 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 10.4986 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 10.4986 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.3493 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 9.2200 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 9.22, max( 10.5, 4.5 ) ]

= 9.2200 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 4.56, 9.22 )

= 9.2200 mm.

Available Nozzle Neck Thickness = 9.6012 mm. --> OK

Stresses on Nozzle due to External and Pressure Loads per the ASME

B31.3 Piping Code (see 319.4.4 and 302.3.5):

Sustained  :     14.9,  Allowable :    117.9 N./mm²  Passed

Expansion  :      0.0,  Allowable :    279.8 N./mm²  Passed

Occasional :     12.4,  Allowable :    156.8 N./mm²  Passed

Shear      :      6.5,  Allowable :     82.5 N./mm²  Passed

Note : The number of cycles on this nozzle was assumed to be 7000 or less for

the determination of the expansion stress allowable.

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld (Impact tested)         :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle Neck to Pad Weld for the Nozzle (Impact tested) :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle Neck to Pad Weld for Reinforcement pad, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 9.6, tr = 1.56, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.24, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Shell to Pad Weld Junction at Pad OD, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 12, tr = 7.5, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.83, Temp. Reduction = 9 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 9.6, tr = 1.56, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.24, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the Nozzle                                :  -104 °C

Gov. MDMT of the Reinforcement Pad                     :   -48 °C

Gov. MDMT of the nozzle to shell joint welded assembly :   -48 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

MDMT of ASME B16.5/47 flange per Matl. Specification       -46 °C

Flange MDMT with Temp reduction per UCS-66(i)(2)           -89 °C

Where the Stress Reduction Ratio per UCS-66(i)(2) is :

Design Pressure/Ambient Rating = 22.00/51.10 = 0.431

Weld Size Calculations, Description: S2 (6in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      6.6012  mm.

Intermediate Calc. for pad/shell Welds   TminPad      9.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          4.6208 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             4.5000 = 0.5*TminPad  7.0700 = 0.7 * Wp mm.

Weld Strength and Weld Loads per UG-41.1, Sketch (a) or (b)

Weld Load [W]:

= max( 0, (A-A1+2*tn*fr1*(E1*t-tr))Sv)

= max( 0,(11.8 - 2.3 + 2 * 6.6 * 0.86 *

(1 * 9 - 7.5 ) )138 )

= 13557.96 Kgf

Note: F is always set to 1.0 throughout the calculation.

Weld Load [W1]:

= (A2+A5+A4-(Wi-Can/.707)²*fr2)*Sv

= ( 1.94 + 15.8 + 1.61 - 0 * 0.86 ) * 138

= 27222.50 Kgf

Weld Load [W2]:

= (A2 + A3 + A4 + (2 * tn * t * fr1)) * Sv

= ( 1.94 + 0 + 0.86 +( 1.02 ) ) * 138

= 5359.09 Kgf

Weld Load [W3]:

= (A2+A3+A4+A5+(2*tn*t*fr1))*S

= ( 1.94 + 0 + 1.61 + 15.8 +( 1.02 ) ) * 138

= 28651.06 Kgf

Strength of Connection Elements for Failure Path Analysis

Shear, Outward Nozzle Weld [Sonw]:

= (pi/2) * Dlo * Wo * 0.49 * Snw

= ( 3.14/2.0 ) * 168 * 10 * 0.49 * 118

= 15572. Kgf

Shear, Pad Element Weld [Spew]:

= (pi/2) * DP * WP * 0.49 * SEW

= ( 3.14/2.0 ) * 300 * 10 * 0.49 * 138

= 32469. Kgf

Shear, Nozzle Wall [Snw]:

= (pi *( Dlr + Dlo )/4 ) * ( Thk - Can ) * 0.7 * Sn

= (3.14 * 80.8 ) *( 9.6 - 3 ) * 0.7 * 118

= 14109. Kgf

Tension, Pad Groove Weld [Tpgw]:

= ( pi/2) * Dlo * Wgpn * 0.74 * Seg

= (3.14/2 ) * 168 * 12 * 0.74 * 138

= 33006. Kgf

Tension, Shell Groove Weld [Tngw]:

= (pi/2) * Dlo * ( T - cas ) * 0.74 * Sng

= ( 3.14/2.0 ) * 168 *( 12 - 3 ) * 0.74 * 138

= 24754. Kgf

Strength of Failure Paths:

PATH11 = ( SPEW + SNW ) = ( 32469 + 14109 ) = 46578 Kgf

PATH22 = ( Sonw + Tpgw + Tngw + Sinw )

= ( 15572 + 33006 + 24754 + 0 ) = 73332 Kgf

PATH33 = ( Spew + Tngw + Sinw )

= ( 32469 + 24754 + 0 ) = 57224 Kgf

Summary of Failure Path Calculations:

Path 1-1 = 46577 Kgf, must exceed W = 13557 Kgf or W1 = 27222 Kgf

Path 2-2 = 73331 Kgf, must exceed W = 13557 Kgf or W2 = 5359 Kgf

Path 3-3 = 57223 Kgf, must exceed W = 13557 Kgf or W3 = 28651 Kgf

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   26.3  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

Nozzle is O.K. for the External Pressure           1.03  bars

The Drop for this Nozzle is : 7.7175 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 199.7175 mm.

Input Echo, WRC107/537 Item     1,       Description: S2 (6in.)     :

Diameter Basis for Vessel                 Vbasis      ID

Cylindrical or Spherical Vessel           Cylsph      Cylindrical

Internal Corrosion Allowance                 Cas      3.0000  mm.

Vessel Diameter                               Dv     925.000  mm.

Vessel Thickness                              Tv      12.000  mm.

Design Temperature                            T1       120.0  °C

Vessel Material                                    SA-516 70

Vessel UNS Number                                     K02700

Vessel Cold S.I. Allowable                   Smc      137.90  N./mm²

Vessel Hot  S.I. Allowable                   Smh      137.90  N./mm²

Note:

Using 2 * Yield for Discontinuity Stress Allowable (Div 2, 4.1.6.3), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Attachment Type                             Type      Round

Diameter Basis for Nozzle                 Nbasis      OD

Corrosion Allowance for Nozzle               Can      3.0000  mm.

Nozzle Diameter                               Dn     168.275  mm.

Nozzle Thickness                              Tn       9.601  mm.

Nozzle Material                                     SA-333 6

Nozzle UNS Number                                     K03006

Nozzle Cold S.I. Allowable                  SNmc      117.90  N./mm²

Nozzle Hot  S.I. Allowable                  SNmh      117.90  N./mm²

Thickness of Reinforcing Pad                Tpad      12.000  mm.

Diameter  of Reinforcing Pad                Dpad     300.000  mm.

Design Internal Pressure                      Dp      22.000  bars

Include Pressure Thrust                                   No

External Forces and Moments in WRC 107/537 Convention:

Radial Load             (SUS)                  P       856.6  Kgf

Longitudinal Shear      (SUS)                 Vl       856.6  Kgf

Circumferential Shear   (SUS)                 Vc       642.5  Kgf

Circumferential Moment  (SUS)                 Mc         0.3  Kg-m.

Longitudinal Moment     (SUS)                 Ml         0.3  Kg-m.

Torsional Moment        (SUS)                 Mt         0.4  Kg-m.

Use Interactive Control                           No

WRC107 Version                           Version  March  1979

Include Pressure Stress Indices per Div. 2                No

Compute Pressure Stress per WRC-368                       No

Local Loads applied at end of Nozzle/Attachment           No

Note:

WRC Bulletin 537 provides equations for the dimensionless curves

found in bulletin 107.  As noted in the foreword to bulletin 537,

"537 is equivalent to WRC 107".  Where 107 is printed in the

results below, "537" can be interchanged with "107".

Stress Attenuation Diameter (for Insert Plates) per WRC 297:

= NozzleOD + 2 * 1.65 * sqrt( Rmean( t - ca ) )

= 168.275 + 2 * 1.65 * sqrt( 470.0 ( 12.0 - 3.0 ) )

= 382.902 mm.

WRC 107 Stress Calculation for SUStained loads:

Radial Load                                   P        856.6  Kgf

Circumferential Shear                        VC        642.5  Kgf

Longitudinal Shear                           VL        856.6  Kgf

Circumferential Moment                       MC          0.3  Kg-m.

Longitudinal Moment                          ML          0.3  Kg-m.

Torsional Moment                             MT          0.4  Kg-m.

Dimensionless Parameters used :   Gamma =   22.67

Dimensionless Loads for Cylindrical Shells at Attachment Junction:

-------------------------------------------------------------------

Curves read for 1979              Beta  Figure    Value   Location

-------------------------------------------------------------------

N(PHI) / ( P/Rm )                0.155   4C        3.739   (A,B)

N(PHI) / ( P/Rm )                0.155   3C        3.087   (C,D)

M(PHI) / ( P )                   0.155   2C1       0.073   (A,B)

M(PHI) / ( P )                   0.155   1C        0.106   (C,D)

N(PHI) / ( MC/(Rm**2 * Beta) )   0.155   3A        0.768   (A,B,C,D)

M(PHI) / ( MC/(Rm    * Beta) )   0.155   1A        0.093   (A,B,C,D)

N(PHI) / ( ML/(Rm**2 * Beta) )   0.155   3B        2.456   (A,B,C,D)

M(PHI) / ( ML/(Rm    * Beta) )   0.155   1B        0.042   (A,B,C,D)

N(x)   / ( P/Rm )                0.155   3C        3.087   (A,B)

N(x)   / ( P/Rm )                0.155   4C        3.739   (C,D)

M(x)   / ( P )                   0.155   1C1       0.111   (A,B)

M(x)   / ( P )                   0.155   2C        0.074   (C,D)

N(x)   / ( MC/(Rm**2 * Beta) )   0.155   4A        1.170   (A,B,C,D)

M(x)   / ( MC/(Rm    * Beta) )   0.155   2A        0.050   (A,B,C,D)

N(x)   / ( ML/(Rm**2 * Beta) )   0.155   4B        0.742   (A,B,C,D)

M(x)   / ( ML/(Rm    * Beta) )   0.155   2B        0.068   (A,B,C,D)

Stress Concentration Factors: Kn = 1.00,   Kb = 1.00

Stresses in the Vessel at the Attachment Junction (N./mm²)

|                    Stress Intensity Values at                                 |

Type of        |                                                                               |

Stress    Load |       Au        Al        Bu        Bl        Cu        Cl        Du        Dl|

------------------------------------------------------------------------------------------------

Circ. Memb. P  |     -3.1|     -3.1|     -3.1|     -3.1|     -2.6|     -2.6|     -2.6|     -2.6|

Circ. Bend. P  |     -8.4|      8.4|     -8.4|      8.4|    -12.1|     12.1|    -12.1|     12.1|

Circ. Memb. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|     -0.0|      0.0|      0.0|

Circ. Memb. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|     -0.0|

Circ. Memb. ML |     -0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Circ. Bend. ML |     -0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|

|                                                                               |

Tot. Circ. Str.|    -11.6|      5.3|    -11.5|      5.2|    -14.7|      9.5|    -14.7|      9.5|

------------------------------------------------------------------------------------------------

Long. Memb. P  |     -2.6|     -2.6|     -2.6|     -2.6|     -3.1|     -3.1|     -3.1|     -3.1|

Long. Bend. P  |    -12.6|     12.6|    -12.6|     12.6|     -8.4|      8.4|     -8.4|      8.4|

Long. Memb. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|     -0.0|      0.0|      0.0|

Long. Bend. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|     -0.0|

Long. Memb. ML |     -0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Long. Bend. ML |     -0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|

|                                                                               |

Tot. Long. Str.|    -15.3|     10.1|    -15.2|     10.0|    -11.6|      5.3|    -11.5|      5.2|

------------------------------------------------------------------------------------------------

Shear VC |      1.1|      1.1|     -1.1|     -1.1|      0.0|      0.0|      0.0|      0.0|

Shear VL |      0.0|      0.0|      0.0|      0.0|     -1.5|     -1.5|      1.5|      1.5|

Shear MT |      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

|                                                                               |

Tot. Shear|      1.1|      1.1|     -1.1|     -1.1|     -1.5|     -1.5|      1.5|      1.5|

------------------------------------------------------------------------------------------------

Str. Int. |     15.6|     10.3|     15.5|     10.3|     15.3|     10.0|     15.3|     10.0|

Dimensionless Parameters used :   Gamma =   52.22

Dimensionless Loads for Cylindrical Shells at Pad edge:

-------------------------------------------------------------------

Curves read for 1979              Beta  Figure    Value   Location

-------------------------------------------------------------------

N(PHI) / ( P/Rm )                0.279   4C        5.662   (A,B)

N(PHI) / ( P/Rm )                0.279   3C        2.676   (C,D)

M(PHI) / ( P )                   0.279   2C1       0.015   (A,B)

M(PHI) / ( P )                   0.279   1C  !     0.065   (C,D)

N(PHI) / ( MC/(Rm**2 * Beta) )   0.279   3A        1.741   (A,B,C,D)

M(PHI) / ( MC/(Rm    * Beta) )   0.279   1A        0.061   (A,B,C,D)

N(PHI) / ( ML/(Rm**2 * Beta) )   0.279   3B        3.690   (A,B,C,D)

M(PHI) / ( ML/(Rm    * Beta) )   0.279   1B        0.011   (A,B,C,D)

N(x)   / ( P/Rm )                0.279   3C        2.676   (A,B)

N(x)   / ( P/Rm )                0.279   4C        5.662   (C,D)

M(x)   / ( P )                   0.279   1C1       0.037   (A,B)

M(x)   / ( P )                   0.279   2C  !     0.034   (C,D)

N(x)   / ( MC/(Rm**2 * Beta) )   0.279   4A        4.862   (A,B,C,D)

M(x)   / ( MC/(Rm    * Beta) )   0.279   2A        0.025   (A,B,C,D)

N(x)   / ( ML/(Rm**2 * Beta) )   0.279   4B        1.882   (A,B,C,D)

M(x)   / ( ML/(Rm    * Beta) )   0.279   2B        0.017   (A,B,C,D)

Note - The ! mark next to the figure name denotes curve value exceeded.

Stress Concentration Factors: Kn = 1.00,   Kb = 1.00

Stresses in the Vessel at the Edge of Reinforcing Pad (N./mm²)

|                    Stress Intensity Values at                                 |

Type of        |                                                                               |

Stress    Load |       Au        Al        Bu        Bl        Cu        Cl        Du        Dl|

------------------------------------------------------------------------------------------------

Circ. Memb. P  |    -11.2|    -11.2|    -11.2|    -11.2|     -5.3|     -5.3|     -5.3|     -5.3|

Circ. Bend. P  |     -9.2|      9.2|     -9.2|      9.2|    -40.7|     40.7|    -40.7|     40.7|

Circ. Memb. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|     -0.0|      0.0|      0.0|

Circ. Memb. MC |      0.0|      0.0|      0.0|      0.0|     -0.1|      0.1|      0.1|     -0.1|

Circ. Memb. ML |     -0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Circ. Bend. ML |     -0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|

|                                                                               |

Tot. Circ. Str.|    -20.5|     -2.0|    -20.4|     -2.0|    -46.1|     35.5|    -45.9|     35.3|

------------------------------------------------------------------------------------------------

Long. Memb. P  |     -5.3|     -5.3|     -5.3|     -5.3|    -11.2|    -11.2|    -11.2|    -11.2|

Long. Bend. P  |    -22.7|     22.7|    -22.7|     22.7|    -20.9|     20.9|    -20.9|     20.9|

Long. Memb. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|     -0.0|      0.0|      0.0|

Long. Bend. MC |      0.0|      0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|     -0.0|

Long. Memb. ML |     -0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Long. Bend. ML |     -0.0|      0.0|      0.0|     -0.0|      0.0|      0.0|      0.0|      0.0|

|                                                                               |

Tot. Long. Str.|    -28.1|     17.4|    -28.0|     17.4|    -32.2|      9.7|    -32.1|      9.7|

------------------------------------------------------------------------------------------------

Shear VC |      1.5|      1.5|     -1.5|     -1.5|      0.0|      0.0|      0.0|      0.0|

Shear VL |      0.0|      0.0|      0.0|      0.0|     -2.0|     -2.0|      2.0|      2.0|

Shear MT |      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

|                                                                               |

Tot. Shear|      1.5|      1.5|     -1.5|     -1.5|     -2.0|     -2.0|      2.0|      2.0|

------------------------------------------------------------------------------------------------

Str. Int. |     28.4|     19.7|     28.3|     19.6|     46.4|     35.6|     46.2|     35.5|

------------------------------------------------------------------------------------------------

WRC 107/537 Stress Summations:

Vessel Stress Summation at Attachment Junction (N./mm²)

|                    Stress Intensity Values at                                 |

Type of        |                                                                               |

Stress    Load |       Au        Al        Bu        Bl        Cu        Cl        Du        Dl|

------------------------------------------------------------------------------------------------

Circ. Pm (SUS) |     47.7|     49.9|     47.7|     49.9|     47.7|     49.9|     47.7|     49.9|

Circ. Pl (SUS) |     -3.2|     -3.2|     -3.1|     -3.1|     -2.6|     -2.6|     -2.6|     -2.6|

Circ. Q  (SUS) |     -8.4|      8.4|     -8.4|      8.4|    -12.1|     12.1|    -12.1|     12.1|

------------------------------------------------------------------------------------------------

Long. Pm (SUS) |     23.8|     23.8|     23.8|     23.8|     23.8|     23.8|     23.8|     23.8|

Long. Pl (SUS) |     -2.6|     -2.6|     -2.6|     -2.6|     -3.1|     -3.1|     -3.1|     -3.1|

Long. Q  (SUS) |    -12.7|     12.7|    -12.6|     12.6|     -8.4|      8.4|     -8.4|      8.4|

------------------------------------------------------------------------------------------------

Shear Pm (SUS) |      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Shear Pl (SUS) |      1.1|      1.1|     -1.1|     -1.1|     -1.5|     -1.5|      1.5|      1.5|

Shear Q  (SUS) |      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Pm (SUS)       |     47.7|     49.9|     47.7|     49.9|     47.7|     49.9|     47.7|     49.9|

------------------------------------------------------------------------------------------------

Pm+Pl (SUS)    |     44.6|     46.8|     44.6|     46.8|     45.2|     47.4|     45.2|     47.4|

------------------------------------------------------------------------------------------------

Pm+Pl+Q (Total)|     36.2|     55.2|     36.2|     55.2|     33.1|     59.5|     33.2|     59.4|

Vessel Stress Summation Comparison (N./mm²):

Type of        |     Max. S.I.     S.I. Allowable     |      Result     |

Stress Int.    |                                      |                 |

-------------------------------------------------------------------------

Pm (SUS)       |         49.89            137.90      |      Passed     |

Pm+Pl (SUS)    |         47.39            206.85      |      Passed     |

Pm+Pl+Q (TOTAL)|         59.52            413.70      |      Passed     |

Because only sustained loads were specified, the Pm+Pl+Q allowable was 3 * Smh.

------------------------------------------------------------------------------------------------

WRC 107/537 Stress Summations:

Vessel Stress Summation at Reinforcing Pad Edge (N./mm²)

|                    Stress Intensity Values at                                 |

Type of        |                                                                               |

Stress    Load |       Au        Al        Bu        Bl        Cu        Cl        Du        Dl|

------------------------------------------------------------------------------------------------

Circ. Pm (SUS) |    112.7|    114.9|    112.7|    114.9|    112.7|    114.9|    112.7|    114.9|

Circ. Pl (SUS) |    -11.3|    -11.3|    -11.2|    -11.2|     -5.3|     -5.3|     -5.3|     -5.3|

Circ. Q  (SUS) |     -9.2|      9.2|     -9.2|      9.2|    -40.8|     40.8|    -40.6|     40.6|

------------------------------------------------------------------------------------------------

Long. Pm (SUS) |     56.4|     56.4|     56.4|     56.4|     56.4|     56.4|     56.4|     56.4|

Long. Pl (SUS) |     -5.3|     -5.3|     -5.3|     -5.3|    -11.3|    -11.3|    -11.2|    -11.2|

Long. Q  (SUS) |    -22.8|     22.8|    -22.7|     22.7|    -21.0|     21.0|    -20.9|     20.9|

------------------------------------------------------------------------------------------------

Shear Pm (SUS) |      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Shear Pl (SUS) |      1.5|      1.5|     -1.5|     -1.5|     -2.0|     -2.0|      2.0|      2.0|

Shear Q  (SUS) |      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|      0.0|

Pm (SUS)       |    112.7|    114.9|    112.7|    114.9|    112.7|    114.9|    112.7|    114.9|

------------------------------------------------------------------------------------------------

Pm+Pl (SUS)    |    101.5|    103.7|    101.5|    103.7|    107.4|    109.6|    107.5|    109.7|

------------------------------------------------------------------------------------------------

Pm+Pl+Q (Total)|     92.2|    112.9|     92.3|    112.9|     66.7|    150.4|     66.9|    150.3|

Vessel Stress Summation Comparison (N./mm²):

Type of        |     Max. S.I.     S.I. Allowable     |      Result     |

Stress Int.    |                                      |                 |

-------------------------------------------------------------------------

Pm (SUS)       |        114.91            137.90      |      Passed     |

Pm+Pl (SUS)    |        109.66            206.85      |      Passed     |

Pm+Pl+Q (TOTAL)|        150.43            413.70      |      Passed     |

Because only sustained loads were specified, the Pm+Pl+Q allowable was 3 * Smh.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: V (2in.)                          From:   70

Pressure for Reinforcement Calculations        P      22.000  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      925.00  mm.

Design Length of Section                       L   2892.0833  mm.

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                    3363.53  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                   SA-350 LF2

Material UNS Number                                   K03011

Material Specification/Type                         Forgings

Allowable Stress at Temperature               Sn      137.90  N./mm²

Allowable Stress At Ambient                  Sna      137.90  N./mm²

Diameter Basis (for tr calc only)                     Inside

Layout Angle                                           90.00  deg

Diameter                                              2.0000  in.

Size and Thickness Basis                              Actual

Actual Thickness                              tn     16.6000  mm.

Flange Material [Normalized]                      SA-350 LF2

Flange Type                                   Long Weld Neck

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    200.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle No Pad, no Inside projection

Reinforcement CALCULATION, Description: V (2in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Inside Diameter Used in Calculation             2.000  in.

Actual Thickness Used in Calculation                   0.654  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.4986 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*R)/(Sn*E-0.6*P) per UG-27 (c)(1)

= (22*28.4)/(138*1-0.6*22)

= 0.4575 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3862  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   113.6000  mm.

Parallel to Vessel Wall, opening length              d    56.8000  mm.

Normal to Vessel Wall (Thickness Limit), no pad   Tlnp    22.5000  mm.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: V (2in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.4575 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 10.4986 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 10.4986 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.3493 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 7.8000 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 7.8, max( 10.5, 4.5 ) ]

= 7.8000 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.46, 7.8 )

= 7.8000 mm.

Available Nozzle Neck Thickness = 16.6000 mm. --> OK

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 12, tr = 7.5, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.83, Temp. Reduction = 9 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Gov. MDMT of the nozzle to shell joint welded assembly :   -48 °C

Weld Size Calculations, Description: V (2in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      9.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          6.0000 = Min per Code 7.0700 = 0.7 * Wo mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   26.3  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

The Drop for this Nozzle is : 1.9110 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 213.9110 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: D (2in.)                          From:   70

Pressure for Reinforcement Calculations        P      22.048  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      925.00  mm.

Design Length of Section                       L   2892.0833  mm.

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                    3363.53  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                   SA-350 LF2

Material UNS Number                                   K03011

Material Specification/Type                         Forgings

Allowable Stress at Temperature               Sn      137.90  N./mm²

Allowable Stress At Ambient                  Sna      137.90  N./mm²

Diameter Basis (for tr calc only)                     Inside

Layout Angle                                          270.00  deg

Diameter                                              2.0000  in.

Size and Thickness Basis                              Actual

Actual Thickness                              tn     16.6000  mm.

Flange Material [Normalized]                      SA-350 LF2

Flange Type                                   Long Weld Neck

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    200.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle No Pad, no Inside projection

Reinforcement CALCULATION, Description: D (2in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Inside Diameter Used in Calculation             2.000  in.

Actual Thickness Used in Calculation                   0.654  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.5152 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*R)/(Sn*E-0.6*P) per UG-27 (c)(1)

= (22*28.4)/(138*1-0.6*22)

= 0.4585 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3862  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   113.6000  mm.

Parallel to Vessel Wall, opening length              d    56.8000  mm.

Normal to Vessel Wall (Thickness Limit), no pad   Tlnp    22.5000  mm.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: D (2in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.4585 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 10.5152 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 10.5152 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.3493 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 7.8000 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 7.8, max( 10.5, 4.5 ) ]

= 7.8000 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.46, 7.8 )

= 7.8000 mm.

Available Nozzle Neck Thickness = 16.6000 mm. --> OK

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 12, tr = 7.52, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.84, Temp. Reduction = 9 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Gov. MDMT of the nozzle to shell joint welded assembly :   -48 °C

Weld Size Calculations, Description: D (2in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      9.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          6.0000 = Min per Code 7.0700 = 0.7 * Wo mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   26.4  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

The Drop for this Nozzle is : 1.9110 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 213.9110 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: PSV (3in.)                        From:   70

Pressure for Reinforcement Calculations        P      22.000  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      925.00  mm.

Design Length of Section                       L   2892.0833  mm.

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                    1483.53  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                     SA-333 6

Material UNS Number                                   K03006

Material Specification/Type                Smls. & wld. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                    Outside

Layout Angle                                           90.00  deg

Diameter                                              3.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                        160

Flange Material                                   SA-350 LF2

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    200.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Pad Material    [Normalized]                       SA-516 70

Pad Allowable Stress at Temperature           Sp      137.90  N./mm²

Pad Allowable Stress At Ambient              Spa      137.90  N./mm²

Diameter of Pad along vessel surface          Dp    190.0000  mm.

Thickness of Pad                              te     12.0000  mm.

Weld leg size between Pad and Shell           Wp     10.0000  mm.

Groove weld depth between Pad and Nozzle    Wgpn     12.0000  mm.

Reinforcing Pad Width                                50.5500  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle With Pad, no Inside projection

Reinforcement CALCULATION, Description: PSV (3in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Outside Diameter Used in Calculation            3.500  in.

Actual Thickness Used in Calculation                   0.383  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.4986 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*Ro)/(Sn*E+0.4*P) per Appendix 1-1 (a)(1)

= (22*44.5)/(118*1+0.4*22)

= 0.8233 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.3989  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   150.8618  mm.

Parallel to Vessel Wall, opening length              d    75.4309  mm.

Normal to Vessel Wall (Thickness Limit), pad side Tlwp    22.5000  mm.

Note: The Pad diameter is greater than the Diameter Limit. The excess will not be considered.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: PSV (3in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.8233 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 10.4986 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 10.4986 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.3493 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 7.8000 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 7.8, max( 10.5, 4.5 ) ]

= 7.8000 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.82, 7.8 )

= 7.8000 mm.

Available Nozzle Neck Thickness = 9.7345 mm. --> OK

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld (Impact tested)         :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle Neck to Pad Weld for the Nozzle (Impact tested) :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle Neck to Pad Weld for Reinforcement pad, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 9.73, tr = 0.82, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.12, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Shell to Pad Weld Junction at Pad OD, Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 12, tr = 7.5, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.83, Temp. Reduction = 9 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 9.73, tr = 0.82, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.12, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the Nozzle                                :  -104 °C

Gov. MDMT of the Reinforcement Pad                     :   -48 °C

Gov. MDMT of the nozzle to shell joint welded assembly :   -48 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

MDMT of ASME B16.5/47 flange per Matl. Specification       -46 °C

Flange MDMT with Temp reduction per UCS-66(i)(2)           -89 °C

Where the Stress Reduction Ratio per UCS-66(i)(2) is :

Design Pressure/Ambient Rating = 22.00/51.10 = 0.431

Weld Size Calculations, Description: PSV (3in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      6.7345  mm.

Intermediate Calc. for pad/shell Welds   TminPad      9.0000  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          4.7142 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Pad Weld             4.5000 = 0.5*TminPad  7.0700 = 0.7 * Wp mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   26.3  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

The Drop for this Nozzle is : 2.1410 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 214.1409 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: LG1 (2in.)                        From:   70

Pressure for Reinforcement Calculations        P      22.000  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      925.00  mm.

Design Length of Section                       L   2892.0833  mm.

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                    1913.53  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                     SA-333 6

Material UNS Number                                   K03006

Material Specification/Type                Smls. & wld. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                     Inside

Layout Angle                                           90.00  deg

Diameter                                              2.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                        160

Flange Material                                   SA-350 LF2

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    150.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

Piping Exit Angle [North Clockwise reference]          270.0  deg

Bend Radius Multiplier                                  1.50

Horizontal Run Length                                  550.0  mm.

Centerline Distance to Tangent                         150.0  mm.

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle No Pad, no Inside projection

Reinforcement CALCULATION, Description: LG1 (2in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Inside Diameter Used in Calculation             1.773  in.

Actual Thickness Used in Calculation                   0.301  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.4986 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*R)/(Sn*E-0.6*P) per UG-27 (c)(1)

= (22*25.5)/(118*1-0.6*22)

= 0.4815 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.2826  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   102.0684  mm.

Parallel to Vessel Wall, opening length              d    51.0342  mm.

Normal to Vessel Wall (Thickness Limit), no pad   Tlnp    11.6135  mm.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: LG1 (2in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.4815 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 10.4986 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 10.4986 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.3493 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 6.4200 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 6.42, max( 10.5, 4.5 ) ]

= 6.4200 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.48, 6.42 )

= 6.4200 mm.

Available Nozzle Neck Thickness = 7.6454 mm. --> OK

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld (Impact tested)         :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 7.65, tr = 0.48, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.1, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the nozzle to shell joint welded assembly :  -104 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

MDMT of ASME B16.5/47 flange per Matl. Specification       -46 °C

Flange MDMT with Temp reduction per UCS-66(i)(2)           -89 °C

Where the Stress Reduction Ratio per UCS-66(i)(2) is :

Design Pressure/Ambient Rating = 22.00/51.10 = 0.431

Weld Size Calculations, Description: LG1 (2in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      4.6454  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          3.2518 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   26.3  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

The Drop for this Nozzle is : 0.9846 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 162.9846 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input,  Nozzle Desc: LG2 (2in.)                        From:   70

Pressure for Reinforcement Calculations        P      22.048  bars

Temperature for Internal Pressure           Temp         120  °C

Design External Pressure                    Pext        1.03  bars

Temperature for External Pressure         Tempex         120  °C

Parent Material [Normalized]                       SA-516 70

Parent Allowable Stress at Temperature        Sv      137.90  N./mm²

Parent Allowable Stress At Ambient           Sva      137.90  N./mm²

Inside Diameter of Cylindrical Shell           D      925.00  mm.

Design Length of Section                       L   2892.0833  mm.

Shell Finished (Minimum) Thickness             t     12.0000  mm.

Shell Internal Corrosion Allowance             c      3.0000  mm.

Shell External Corrosion Allowance            co      0.0000  mm.

Distance from Bottom/Left Tangent                    1913.53  mm.

User Entered Minimum Design Metal Temperature         -45.00  °C

Type of Element Connected to the Parent : Nozzle

Material        [Impact Tested]                     SA-333 6

Material UNS Number                                   K03006

Material Specification/Type                Smls. & wld. pipe

Allowable Stress at Temperature               Sn      117.90  N./mm²

Allowable Stress At Ambient                  Sna      117.90  N./mm²

Diameter Basis (for tr calc only)                     Inside

Layout Angle                                          270.00  deg

Diameter                                              2.0000  in.

Size and Thickness Basis                             Minimum

Nominal Thickness                                        160

Flange Material                                   SA-350 LF2

Flange Type                                 Weld Neck Flange

Corrosion Allowance                          can      3.0000  mm.

Joint Efficiency of Shell Seam at Nozzle      E1        1.00

Joint Efficiency of Nozzle Neck               En        1.00

Outside Projection                            ho    150.0000  mm.

Weld leg size between Nozzle and Pad/Shell    Wo     10.0000  mm.

Groove weld depth between Nozzle and Vessel Wgnv     12.0000  mm.

Inside Projection                              h      0.0000  mm.

Weld leg size, Inside Element to Shell        Wi      0.0000  mm.

Flange Class                                             300

Flange Grade                                          GR 1.1

Piping Exit Angle [North Clockwise reference]           90.0  deg

Bend Radius Multiplier                                  1.50

Horizontal Run Length                                  550.0  mm.

Centerline Distance to Tangent                         150.0  mm.

The Pressure Design option was Design Pressure + static head.

Nozzle Sketch (may not represent actual weld type/configuration)

Insert/Set-in Nozzle No Pad, no Inside projection

Reinforcement CALCULATION, Description: LG2 (2in.)

ASME Code, Section VIII, Div. 1, 2019, UG-37 to UG-45

Actual Inside Diameter Used in Calculation             1.773  in.

Actual Thickness Used in Calculation                   0.301  in.

Nozzle input data check completed without errors.

Reqd thk per UG-37(a) of Cylindrical Shell, Tr [Int. Press]

= (P*R)/(Sv*E-0.6*P) per UG-27 (c)(1)

= (22*466)/(138*1-0.6*22)

= 7.5152 mm.

Reqd thk per UG-37(a) of Nozzle Wall, Trn [Int. Press]

= (P*R)/(Sn*E-0.6*P) per UG-27 (c)(1)

= (22*25.5)/(118*1-0.6*22)

= 0.4826 mm.

Required Nozzle thickness under External Pressure per UG-28 :  0.2826  mm.

UG-40, Limits of Reinforcement : [Internal Pressure]

Parallel to Vessel Wall (Diameter Limit)            Dl   102.0684  mm.

Parallel to Vessel Wall, opening length              d    51.0342  mm.

Normal to Vessel Wall (Thickness Limit), no pad   Tlnp    11.6135  mm.

Note:

Taking a UG-36(c)(3)(a) exemption for nozzle: LG2 (2in.).

This calculation is valid for nozzles that meet all the requirements of

paragraph UG-36.  Please check the Code carefully, especially for nozzles

that are not isolated or do not meet Code spacing requirements. To force

the computation of areas for small nozzles go to Tools->Configuration

and check the box to force the UG-37 small nozzle area calculation or

force the Appendix 1-10 computation in Nozzle Design Options.

UG-45 Minimum Nozzle Neck Thickness Requirement: [Int. Press.]

Wall Thickness for Internal/External pressures      ta = 3.4826 mm.

Wall Thickness per UG16(b),                      tr16b = 4.5000 mm.

Wall Thickness, shell/head, internal pressure     trb1 = 10.5152 mm.

Wall Thickness                  tb1 = max(trb1, tr16b) = 10.5152 mm.

Wall Thickness, shell/head, external pressure     trb2 = 3.3493 mm.

Wall Thickness                  tb2 = max(trb2, tr16b) = 4.5000 mm.

Wall Thickness per table UG-45                     tb3 = 6.4200 mm.

Determine Nozzle Thickness candidate [tb]:

= min[ tb3, max( tb1,tb2) ]

= min[ 6.42, max( 10.5, 4.5 ) ]

= 6.4200 mm.

Minimum Wall Thickness of Nozzle Necks [tUG-45]:

= max( ta, tb )

= max( 3.48, 6.42 )

= 6.4200 mm.

Available Nozzle Neck Thickness = 7.6454 mm. --> OK

Nozzle Junction Minimum Design Metal Temperature (MDMT) Calculations:

Nozzle Neck to Flange Weld (Impact tested)         :

----------------------------------------------------------------------

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Calculated Minimum Design Metal Temperature               -104 °C

Nozzle-Shell/Head Weld (UCS-66(a)1(b)), Curve: D

----------------------------------------------------------------------

Govrn. thk, tg = 7.65, tr = 0.48, c = 3 mm., E* = 1

Thickness Ratio = tr *(E*)/(tg - c) = 0.1, Temp. Reduction = 78 °C

Min Metal Temp. w/o impact per UCS-66, Curve D             -48 °C

Min Metal Temp. at Required thickness (UCS 66.1)          -104 °C

Gov. MDMT of the nozzle to shell joint welded assembly :  -104 °C

ANSI Flange MDMT including Temperature reduction per UCS-66.1:

MDMT of ASME B16.5/47 flange per Matl. Specification       -46 °C

Flange MDMT with Temp reduction per UCS-66(i)(2)           -89 °C

Where the Stress Reduction Ratio per UCS-66(i)(2) is :

Design Pressure/Ambient Rating = 22.05/51.10 = 0.431

Weld Size Calculations, Description: LG2 (2in.)

Intermediate Calc. for nozzle/shell Welds   Tmin      4.6454  mm.

Results Per UW-16.1:

Required Thickness    Actual Thickness

Nozzle Weld          3.2518 = 0.7 * tmin.  7.0700 = 0.7 * Wo mm.

Skipping the nozzle attachment weld strength calculations.

Per UW-15(b)(2) the nozzles exempted by UG-36(c)(3)(a)

(small nozzles) do not require a weld strength check.

Maximum Allowable Pressure for this Nozzle at this Location:

Converged Max. Allow. Pressure in Operating case   26.4  bars

Note: The MAWP of this junction was limited by the parent Shell/Head.

The Drop for this Nozzle is : 0.9846 mm.

The Cut Length for this Nozzle is, Drop + Ho + H + T : 162.9846 mm.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input Echo, Tubesheet Number     1,         Description: Tubesheet

Shell Data:

Main Shell Description: Port Barrel

Shell Maximum Design Pressure            Psd,max       22.00  bars

Shell Maximum Operating Pressure        Psox,max       22.00  bars

Shell Minimum Operating Pressure        Psox,min        0.00  bars

Shell Thickness                               ts     12.0000  mm.

Shell Internal Corrosion Allowance           cas      3.0000  mm.

Shell External Corrosion Allowance         caext      0.0000  mm.

Inside Diameter of Shell                      Ds     600.000  mm.

Shell Temperature for Internal Pressure       Ts      120.00  °C

Shell Material                                     SA-516 70

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Shell Material UNS Number                             K02700

Shell Allowable Stress at Temperature         Ss      137.90  N./mm²

Shell Allowable Stress at Ambient                     137.90  N./mm²

Channel Description: CH. Barrel

Channel Type:                                      Cylinder

Channel Maximum Design Pressure          Ptd,max        6.80  bars

Channel Maximum Operating Pressure      Ptox,max        6.80  bars

Channel Minimum Operating Pressure      Ptox,min        0.00  bars

Channel Thickness                             tc     10.0000  mm.

Channel Corrosion Allowance                  cac      3.0000  mm.

Inside Diameter of Channel                    Dc     600.000  mm.

Channel Design Temperature                 TEMPC       85.00  °C

Channel Material                                   SA-516 70

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Channel Material UNS Number                           K02700

Channel Allowable Stress at Temperature       Sc      137.90  N./mm²

Channel Allowable Stress at Ambient                   137.90  N./mm²

Tube Data:

Number of Tube Holes                          Nt         376

Tube Wall Thickness                           et      1.6500  mm.

Tube Outside Diameter                          D     19.0500  mm.

Total Straight Tube Length                    Lt     2500.00  mm.

Straight Tube Length (bet. inner tubsht faces) L     2440.00  mm.

Design Temperature of the Tubes                       120.00  °C

Tube Material                                       SA-334 6

Tube Material UNS Number                              K03006

Is this a Welded Tube                                     No

Tube Material Specification used           Smls. & wld. tube

Tube Allowable Stress at Temperature                  117.90  N./mm²

Tube Allowable Stress At Ambient                      117.90  N./mm²

Tube Yield Stress At design Temperature      Syt      217.36  N./mm²

Tube Pitch (Center to Center Spacing)          P     23.8130  mm.

Tube Layout Pattern                               Triangular

Radius to Outermost Tube Hole Center          ro     283.510  mm.

Largest Center-to-Center Tube Distance        Ul     52.3870  mm.

Length of Expanded Portion of Tube           ltx     57.0000  mm.

Tube-side pass partition groove depth         hg      5.0000  mm.

Tubesheet Data:

Tubesheet TYPE:  U-tube, Gasketed both Sides, Conf. d

Tubesheet Design Metal Temperature             T      120.00  °C

Tubesheet Material                                SA-350 LF2

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-350 LF2

Tubesheet Material UNS Number                         K03011

Tubesheet Allowable Stress at Temperature      S      137.90  N./mm²

Tubesheet Allowable Stress at Ambient         Tt      137.90  N./mm²

Thickness of Tubesheet                         h     60.0000  mm.

Tubesheet Corr. Allowance (Shell side)      Cats      3.0000  mm.

Tubesheet Corr. Allowance (Channel side)    Catc      3.0000  mm.

Tubesheet Outside Diameter                     A     650.000  mm.

Dimension G for the Channel Side              Gc     637.151  mm.

Area of the Untubed Lanes                     AL       425.5  cm²

Junction Stress Reduction option              Increase Tubesheet thickness

Perform Differential Pressure Design                      NO

Run Multiple Load Cases                                  YES

Additional Data for Gasketed Tubesheets:

Tubesheet Gasket on which Side                          Both

Flange Outside Diameter                        A     760.000  mm.

Flange Inside Diameter                         B     600.000  mm.

Flange Face Outside Diameter                 Fod     653.000  mm.

Flange Face Inside Diameter                  Fid     600.000  mm.

Gasket Outside Diameter                       Go     650.000  mm.

Gasket Inside Diameter                        Gi     624.000  mm.

Small end Hub thk.                            g0     12.0000  mm.

Large end Hub thk.                            g1     18.0000  mm.

Gasket Factor,                                 m        3.00

Gasket Design Seating Stress                   y       69.00  N./mm²

Flange Facing Sketch                          Code Sketch 1b

Column for Gasket Seating                     Code Column II

Gasket Thickness                              tg      4.5000  mm.

Full face Gasket Flange Option               Program Selects

Bolting Information:

Diameter of Bolt Circle                        C     705.000  mm.

Nominal Bolt Diameter                         dB     22.2250  mm.

Type of Thread Series                         TEMA Thread Series

Number of Bolts                                n          20

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature          Sb      172.38  N./mm²

Bolt Allowable Stress At Ambient              Sa      172.38  N./mm²

Weld between Flange and Shell/Channel                 0.0000  mm.

Alternate Flange Operating Bolt Load, Wm1            88967.88 Kgf

Alternate Flange Seating Bolt Load, Wm2              90480.76 Kgf

Alternate Flange Design Bolt Load, W                 92754.98 Kgf

Tubesheet Integral with                                 None

Tubesheet Extended as Flange                              No

ASME TubeSheet Results per Part UHX, 2019

Elasticity/Expansion Material Properties :

Shell      - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature      120.0 °C      0.19691E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Channel    - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature       85.0 °C      0.19904E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Tubes      - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Tubsht. Design Temp.    120.0 °C      0.19691E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

TubeSheet  - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature      120.0 °C      0.19691E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Tube Required Thickness under Internal Pressure (Tubeside pressure):

Thickness Due to Internal Pressure:

= (P*(D/2-CAE)) / (S*E+0.4*P) per Appendix 1-1 (a)(1)

= (6.8*(19/2-0)/(118*1+0.4*6.8)

= 0.0548 + 0.0000 = 0.0548 mm.

Tube Required Thickness under External Pressure (Shellside pressure) :

External Pressure Chart     CS-2             at       120.00  °C

Elastic Modulus for Material                    199943392.00  KPa.

Results for Max. Allowable External Pressure (Emawp):

TCA        ODCA     SLEN       D/T       L/D   Factor A        B

1.6500     19.05   2723.51     11.55   50.0000  0.0082522        122.73

EMAWP = (4*B)/(3*(D/T)) = ( 4 *123 )/( 3 *11.5 ) = 142 bars

Results for Reqd Thickness for Ext. Pressure (Tca):

TCA        ODCA     SLEN       D/T       L/D   Factor A        B

0.4699     19.05   2723.51     40.54   50.0000  0.0006692         66.90

EMAWP = (4*B)/(3*(D/T)) = ( 4 *66.9 )/( 3 *40.5 ) = 22 bars

Summary of Tube Required Thickness Results:

Total Required Thickness including Corrosion all.           0.4699  mm.

Allowable Internal Pressure at Corroded thickness           219.44  bars

Required Internal Design Pressure                             6.80  bars

Allowable External Pressure at Corroded thickness           141.73  bars

Required External Design Pressure                            22.00  bars

Required Thickness due to Shell Side pressure               0.4699  mm.

-----------------------------------------------------------------

Detailed Results for load Case D3 un-corr. (Psd,max + Ptd,max)

-----------------------------------------------------------------

Intermediate Calculations For Gasketed Tubesheets:

ASME Code, Section VIII Division 1, 2019

Gasket Contact Width,       N = (Goc-Gic) / 2            13.000  mm.

Basic Gasket Width,        b0 = N / 2.0                   6.500  mm.

Effective Gasket Width,     b = SQRT(b0) * 2.5            6.422  mm.

Gasket Reaction Diameter,   G = Go-2.0*b                637.156  mm.

Flange Design Bolt Load, Seating Condition    W  :    92754.98  Kgf

Flange Design Bolt Load, Operating Condition  Wm1:    88836.14  Kgf

Results for ASME U-tube Tubesheet Calculations for Configuration d,

Per Edition 2019, Original Thickness :

Minimum Required Thickness for Shear [HreqS]:

= 1/(4 * Mu) * (Do/(min(0.8*S, 0.533*Sy)))[Ps - Pt] + Cats + Catc

= 1/(4 * 0.2 ) * (586/110 )[22 - 6.8 ] + 0

= 10.0934 mm.

UHX-12.5.1 Step 1:

Compute the Equivalent Outer Tube Limit Circle Diameter [Do]:

= 2 * ro + dt

= 2 * 284 + 19 = 586 mm.

Determine the Basic Ligament Efficiency for Shear [mu]:

= (p - dt) / p

= (23.8 - 19 )/23.8 = 0.2

UHX-12.5.2 Step 2:

Compute the Ratio [Rhos]:

= Gs / Do (Configurations d, e, f)

= 637/586 = 1.09

Compute the Ratio [Rhoc]:

= Gc / Do (Configurations d)

= 637/586 = 1.09

Moment on Tubesheet due to Pressures (Ps, Pt) [Mts]:

= Do²/16 * [(Rhos-1)*(Rhos²+1)* Ps - (Rhoc-1) * (Rhoc²+1) * Pt ]

= 586²/16 * [ (1.09 - 1) * (1.09² + 1) * 22 -

(1.09 - 1) * (1.09² + 1) * 6.8 ]

= 62062.8672 bars*mm.²

UHX-12.5.3 Step 3, Determination of Effective Elastic Properties :

Compute the Ratio [rho]:

= ltx/h = 57/60 = 0.95 ( must be 0 <= rho <= 1 )

Compute the Effective Tube Hole Diameter [d*]:

= max( dt - 2tt*( Et/E )( St/S )( rho ), dt - 2tt)

= max( 19 -2*1.65 *(196910448/196910448 )*

( 118/138 )*(0.95 ), 19 -2*1.65 )

= 16.3696 mm.

Compute the Effective Tube Pitch [p*]:

= p / sqrt( 1 - 4 * min( AL * CNV_factor, 4*Do*p)/(Pi * Do²) )

= 23.8/sqrt( 1 - 4 * min( 425 *100, 4*586 *23.8 )

(3.141* 586²) )

= 25.9469 mm.

Compute the Effective Ligament Efficiency for Bending [mu*]:

= (p* - d*)/p* = (25.9 - 16.4 )/25.9 = 0.37

E*/E and nu* for Triangular pattern from Fig. UHX-11.3.

h/p =   2.519632 ;  mu* =   0.369112

E*/E =   0.372514 ;  nu* =   0.319336 ;  E* = 73351928. KPa.

Note: As h/p (2.520) is > 2, data values for h/p = 2 were used.

Skip Step 4 for Configuration d :

UHX-12.5.5 Step 5:

Diameter ratio [K]:

= A/Do = 650/586 = 1.11

Determine Coefficient [F]:

= (1 - nu*)/E* * ( E * ln(K) )

= (1 - 0.32 )/73351928 * ( 196910448 * ln(1.11 ) )

= 0.1892

UHX-12.5.6 Step 6:

Moment Acting on Unperforated Tubesheet Rim [M*]

= Mts + W* * (Gc - Gs)/(2 * pi * Do)

= 62063 + 88968 * (637 - 637 )/(2 * pi * 586 )

= 62062.8672 bars*mm.²

Note: W* is the maximum of the bolt loads between the shell and channel sides.

UHX-12.5.7 Step 7:

Maximum Bending Moment acting on Periphery of Tubesheet [Mp]:

= ((M*) - Do²/32 * F * (Ps - Pt) ) / (1 + F)

= ((62063 ) - 586²/32 * 0.19 * (22 - 6.8 ) )/(1 + 0.19 )

= 26235.0996 bars*mm.²

Maximum Bending Moment acting on Center of Tubesheet [Mo]:

= Mp + Do²/64 * (3 + rnu*)(Ps - Pt)

= 26235 + 586²/64 * (3 + 0.32 )(22 - 6.8 )

= 297013.3750 bars*mm.²

Maximum Bending Moment acting on Tubesheet [M]:

= Max( abs(Mp), abs(Mo) )

= Max( abs(26235 ), abs(297013 ) )

= 297013.3750 bars*mm.²

UHX-12.5.8 Step 8:

Tubesheet Bending Stress at Original Thickness:

= 6 * M / ( (mu*) * ( h - hg')² )

= 6 * 297013/( (0.37 ) * ( 60 - 5 )² )

= 159.6132 N./mm²

The Allowable Tubesheet Bending Stress [SigmaAll]:

= 2 * S = 2 * 138 = 276 N./mm²

Tubesheet Bending Stress at Final Thickness [Sigma]:

= 6 * M / ( (mu*) * ( h - hg')²

= 6 * 297361/( (0.37 ) * ( 46.6 - 5 )²

= 275.7786 N./mm²

Required Tubesheet Thickness, for Bending Stress [HreqB]:

= H + CATS + CATC = 46.6 + 0 + 0 = 46.6 mm.

Required Tubesheet Thickness for Given Loadings (includes CA) [Hreq]:

= Max( HreqB, HreqS ) = Max( 46.6, 10.1 ) = 46.6 mm.

UHX-12.5.9 Step 9:

abs(Ps - Pt) = abs(22 - 6.8 ) = 15.2 bars

Shear Stress check [Tau_limit]:

= 3.2 * S * mu * h/Do

= 3.2 * 138 * 0.2 * 60/586 = 90.4 bars

Average Shear Stress at the Outer Edge of Perforated Region [Tau]:

= 1/(4* Mu) * (Do/h) * [Ps - Pt]

= 1/(4*0.2)*(586/60)*[22-6.8]N./mm²

= 18.56 N./mm²

Note: Analysis Completed for Tubesheet Configuration d.

Stress/Force summary for loadcase D3 un-corr. (Psd,max + Ptd,max):

------------------------------------------------------------------------

Stress Description            Actual         Allowable    Pass/Fail

------------------------------------------------------------------------

Tubesheet bend. stress             159.6  <=      275.8 N./mm²    Ok

Tubesheet shear stress              18.6  <=      110.3 N./mm²    Ok

------------------------------------------------------------------------

Thickness results for loadcase D3 un-corr. (Psd,max + Ptd,max):

Thickness (mm.)                         Required    Actual  P/F   |

------------------------------------------------------------------------------

Tubesheet Thickness :                               46.562     60.000   Ok   |

U-Tube Tubesheet results per ASME UHX-12 2019

Results for  6 Load Cases:

--Reqd. Thk. + CA       ---- Tubesheet  Stresses       Case    Pass/

Case#  Tbsht     Extnsn    Bend   Allwd    Shear  Allwd       Type    Fail

----------------------------------------------------------------------------

D1uc  32.806       0.962      71     276       8     110    Ps+Pt D1      Ok

D2uc  55.009       3.111     231     276      27     110    Ps+Pt D2      Ok

D3uc  46.562       2.150     160     276      19     110    Ps+Pt D3      Ok

D1c   35.858       0.962      79     276       9     110    Ps+Pt-c D1    Ok

D2c   58.003       3.111     255     276      30     110    Ps+Pt-c D2    Ok

D3c   49.579       2.150     176     276      21     110    Ps+Pt-c D3    Ok

----------------------------------------------------------------------------

Max:  58.0031       3.111  mm.      0.925           0.271  (Str. Ratio)

Load Case Definitions:

[Ps & Pt]:

Shell-side and Tube-side Design or Operating Pressures

derived from Psd,min Ptd,max, Psox,min, Ptox,max etc. per the

Load Case Tables

[c]:

With or Without Corrosion Allowance

[D1, D2, D3]:

Design Load Cases using the Maximum and Minimum Design Pressures

[D4]:

Design Load Case using the Minimum (Vacuum) Pressures (if specified)

Note:

Because there was no net pressure differential across the tubesheet due to

the specified pressures psd,min and ptd,min; load case D4 was not processed as

the resulting tubesheet bending stress would be zero.

Summary of Thickness Comparisons for  6 Load Cases:

Thickness (mm.)                         Required    Actual  P/F   |

------------------------------------------------------------------------------

Tubesheet Thickness :                               58.003     60.000   Ok   |

Tubesheet Thickness Flanged Extension :              3.111     50.000   Ok   |

Tube Thickness :                                     0.470      1.650   Ok   |

Tubesheet MAWP used to Compute Hydrotest Pressure:

Stress / Force           | Tubeside   |0 shellside| Shellside  |0 tubeside |

Condition              |    MAWP    |Stress Rat.|    MAWP    |Stress Rat.|

---------------------------------------------------------------------------------

Tubesheet Bending Stress      |     23.795 |     1.000 |     23.794 |     1.000 |

Tubesheet Shear Stress        |     81.319 |     1.000 |     81.319 |     1.000 |

Tube Pressure Stress          |    219.436 |     1.000 |    141.727 |     1.000 |

---------------------------------------------------------------------------------

Minimum MAWP                  |     23.795 |           |     23.794 |           |

Tubesheet MAPnc used to Compute Hydrotest Pressure:

Stress / Force           | Tubeside   |0 shellside| Shellside  |0 tubeside |

Condition              |    MAPnc   |Stress Rat.|    MAPnc   |Stress Rat.|

---------------------------------------------------------------------------------

Tubesheet Bending Stress      |     26.264 |     1.000 |     26.264 |     1.000 |

Tubesheet Shear Stress        |     90.355 |     1.000 |     90.355 |     1.000 |

Tube Pressure Stress          |    219.436 |     1.000 |    141.727 |     1.000 |

---------------------------------------------------------------------------------

Minimum MAPnc                 |     26.264 |           |     26.264 |           |

(*) All load cases were analyzed to compute the MAWP for determining the test pressure.

Tubesheet MDMT Calculations:

Note: The loading conditions from this case will be used to determine

the tubesheet MDMT.

Determine the governing MDMT considering the governing condition:

Governing thickness on the shell side per figure UCS-66.3 (c):

= tubesheet thickness/4

= 60/4

= 15.000 mm.

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

where the MDMT reduction ratio per UCS 66 (b)(1)(b) is:

= max( pt/Tubeside MAPnc, ps/Shellside MAPnc ), must be <= 1

= max( 6.8/26.3, 22/26.3 )

= 0.838

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input Echo, Tubesheet Number     2,         Description: Tubesheet

Shell Data:

Main Shell Description: Port Barrel

Shell Maximum Design Pressure            Psd,max       22.00  bars

Shell Maximum Operating Pressure        Psox,max       22.00  bars

Shell Minimum Operating Pressure        Psox,min        0.00  bars

Shell Thickness                               ts     12.0000  mm.

Shell Internal Corrosion Allowance           cas      3.0000  mm.

Shell External Corrosion Allowance         caext      0.0000  mm.

Inside Diameter of Shell                      Ds     600.000  mm.

Shell Temperature for Internal Pressure       Ts      -45.00  °C

Shell Material                                     SA-516 70

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Shell Material UNS Number                             K02700

Shell Allowable Stress at Temperature         Ss      137.90  N./mm²

Shell Allowable Stress at Ambient                     137.90  N./mm²

Channel Description: CH. Barrel

Channel Type:                                      Cylinder

Channel Maximum Design Pressure          Ptd,max        6.80  bars

Channel Maximum Operating Pressure      Ptox,max        6.80  bars

Channel Minimum Operating Pressure      Ptox,min        0.00  bars

Channel Thickness                             tc     10.0000  mm.

Channel Corrosion Allowance                  cac      3.0000  mm.

Inside Diameter of Channel                    Dc     600.000  mm.

Channel Design Temperature                 TEMPC      -29.00  °C

Channel Material                                   SA-516 70

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Channel Material UNS Number                           K02700

Channel Allowable Stress at Temperature       Sc      137.90  N./mm²

Channel Allowable Stress at Ambient                   137.90  N./mm²

Tube Data:

Number of Tube Holes                          Nt         376

Tube Wall Thickness                           et      1.6500  mm.

Tube Outside Diameter                          D     19.0500  mm.

Total Straight Tube Length                    Lt     2500.00  mm.

Straight Tube Length (bet. inner tubsht faces) L     2440.00  mm.

Design Temperature of the Tubes                       -45.00  °C

Tube Material                                       SA-334 6

Tube Material UNS Number                              K03006

Is this a Welded Tube                                     No

Tube Material Specification used           Smls. & wld. tube

Tube Allowable Stress at Temperature                  117.90  N./mm²

Tube Allowable Stress At Ambient                      117.90  N./mm²

Tube Yield Stress At design Temperature      Syt      241.32  N./mm²

Tube Pitch (Center to Center Spacing)          P     23.8130  mm.

Tube Layout Pattern                               Triangular

Radius to Outermost Tube Hole Center          ro     283.510  mm.

Largest Center-to-Center Tube Distance        Ul     52.3870  mm.

Length of Expanded Portion of Tube           ltx     57.0000  mm.

Tube-side pass partition groove depth         hg      5.0000  mm.

Tubesheet Data:

Tubesheet TYPE:  U-tube, Gasketed both Sides, Conf. d

Tubesheet Design Metal Temperature             T      -45.00  °C

Tubesheet Material                                SA-350 LF2

Tubesheet Material UNS Number                         K03011

Tubesheet Allowable Stress at Temperature      S      223.40  N./mm²

Tubesheet Allowable Stress at Ambient         Tt      223.40  N./mm²

Thickness of Tubesheet                         h     60.0000  mm.

Tubesheet Corr. Allowance (Shell side)      Cats      3.0000  mm.

Tubesheet Corr. Allowance (Channel side)    Catc      3.0000  mm.

Tubesheet Outside Diameter                     A     650.000  mm.

Dimension G for the Channel Side              Gc     637.151  mm.

Area of the Untubed Lanes                     AL       425.5  cm²

Junction Stress Reduction option              Increase Tubesheet thickness

Perform Differential Pressure Design                      NO

Run Multiple Load Cases                                  YES

Additional Data for Gasketed Tubesheets:

Tubesheet Gasket on which Side                          Both

Flange Outside Diameter                        A     760.000  mm.

Flange Inside Diameter                         B     600.000  mm.

Flange Face Outside Diameter                 Fod     653.000  mm.

Flange Face Inside Diameter                  Fid     600.000  mm.

Gasket Outside Diameter                       Go     650.000  mm.

Gasket Inside Diameter                        Gi     624.000  mm.

Small end Hub thk.                            g0     12.0000  mm.

Large end Hub thk.                            g1     18.0000  mm.

Gasket Factor,                                 m        3.00

Gasket Design Seating Stress                   y       69.00  N./mm²

Flange Facing Sketch                          Code Sketch 1b

Column for Gasket Seating                     Code Column II

Gasket Thickness                              tg      4.5000  mm.

Full face Gasket Flange Option               Program Selects

Bolting Information:

Diameter of Bolt Circle                        C     705.000  mm.

Nominal Bolt Diameter                         dB     22.2250  mm.

Type of Thread Series                         TEMA Thread Series

Number of Bolts                                n          20

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature          Sb      172.38  N./mm²

Bolt Allowable Stress At Ambient              Sa      172.38  N./mm²

Weld between Flange and Shell/Channel                 0.0000  mm.

Alternate Flange Operating Bolt Load, Wm1            88967.88 Kgf

Alternate Flange Seating Bolt Load, Wm2              90480.76 Kgf

Alternate Flange Design Bolt Load, W                 92754.98 Kgf

Tubesheet Integral with                                 None

Tubesheet Extended as Flange                              No

ASME TubeSheet Results per Part UHX, 2019

Elasticity/Expansion Material Properties :

Shell      - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature      -45.0 °C      0.20704E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Channel    - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature      -29.0 °C      0.20599E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Tubes      - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Tubsht. Design Temp.    -45.0 °C      0.20704E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

TubeSheet  - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature      -45.0 °C      0.20704E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Tube Required Thickness under Internal Pressure (Tubeside pressure):

Thickness Due to Internal Pressure:

= (P*(D/2-CAE)) / (S*E+0.4*P) per Appendix 1-1 (a)(1)

= (6.8*(19/2-0)/(118*1+0.4*6.8)

= 0.0548 + 0.0000 = 0.0548 mm.

Tube Required Thickness under External Pressure (Shellside pressure) :

External Pressure Chart     CS-2             at       -45.00  °C

Elastic Modulus for Material                    199943392.00  KPa.

Results for Max. Allowable External Pressure (Emawp):

TCA        ODCA     SLEN       D/T       L/D   Factor A        B

1.6500     19.05   2723.51     11.55   50.0000  0.0082522        122.73

EMAWP = (4*B)/(3*(D/T)) = ( 4 *123 )/( 3 *11.5 ) = 142 bars

Results for Reqd Thickness for Ext. Pressure (Tca):

TCA        ODCA     SLEN       D/T       L/D   Factor A        B

0.4699     19.05   2723.51     40.54   50.0000  0.0006692         66.90

EMAWP = (4*B)/(3*(D/T)) = ( 4 *66.9 )/( 3 *40.5 ) = 22 bars

Summary of Tube Required Thickness Results:

Total Required Thickness including Corrosion all.           0.4699  mm.

Allowable Internal Pressure at Corroded thickness           219.44  bars

Required Internal Design Pressure                             6.80  bars

Allowable External Pressure at Corroded thickness           141.73  bars

Required External Design Pressure                            22.00  bars

Required Thickness due to Shell Side pressure               0.4699  mm.

U-Tube Tubesheet results per ASME UHX-12 2019

Results for  6 Load Cases:

--Reqd. Thk. + CA       ---- Tubesheet  Stresses       Case    Pass/

Case#  Tbsht     Extnsn    Bend   Allwd    Shear  Allwd       Type    Fail

----------------------------------------------------------------------------

D1uc  28.074       0.594      79     447       8     132    Ps+Pt D1      Ok

D2uc  46.475       1.920     256     447      27     132    Ps+Pt D2      Ok

D3uc  39.472       1.327     177     447      19     132    Ps+Pt D3      Ok

D1c   31.041       0.594      88     447       9     132    Ps+Pt-c D1    Ok

D2c   49.489       1.920     284     447      30     132    Ps+Pt-c D2    Ok

D3c   42.502       1.327     196     447      21     132    Ps+Pt-c D3    Ok

----------------------------------------------------------------------------

Max:  49.4892       1.920  mm.      0.636           0.226  (Str. Ratio)

Load Case Definitions:

[Ps & Pt]:

Shell-side and Tube-side Design or Operating Pressures

derived from Psd,min Ptd,max, Psox,min, Ptox,max etc. per the

Load Case Tables

[c]:

With or Without Corrosion Allowance

[D1, D2, D3]:

Design Load Cases using the Maximum and Minimum Design Pressures

[D4]:

Design Load Case using the Minimum (Vacuum) Pressures (if specified)

Note:

Because there was no net pressure differential across the tubesheet due to

the specified pressures psd,min and ptd,min; load case D4 was not processed as

the resulting tubesheet bending stress would be zero.

Summary of Thickness Comparisons for  6 Load Cases:

Thickness (mm.)                         Required    Actual  P/F   |

------------------------------------------------------------------------------

Tubesheet Thickness :                               49.489     60.000   Ok   |

Tubesheet Thickness Flanged Extension :              1.920     50.000   Ok   |

Tube Thickness :                                     0.470      1.650   Ok   |

Tubesheet MAWP used to Compute Hydrotest Pressure:

Stress / Force           | Tubeside   |0 shellside| Shellside  |0 tubeside |

Condition              |    MAWP    |Stress Rat.|    MAWP    |Stress Rat.|

---------------------------------------------------------------------------------

Tubesheet Bending Stress      |     34.584 |     1.000 |     34.583 |     1.000 |

Tubesheet Shear Stress        |     97.515 |     1.000 |     97.515 |     1.000 |

Tube Pressure Stress          |    219.436 |     1.000 |    141.727 |     1.000 |

---------------------------------------------------------------------------------

Minimum MAWP                  |     34.584 |           |     34.583 |           |

Tubesheet MAPnc used to Compute Hydrotest Pressure:

Stress / Force           | Tubeside   |0 shellside| Shellside  |0 tubeside |

Condition              |    MAPnc   |Stress Rat.|    MAPnc   |Stress Rat.|

---------------------------------------------------------------------------------

Tubesheet Bending Stress      |     38.329 |     1.000 |     38.329 |     1.000 |

Tubesheet Shear Stress        |    108.358 |     1.000 |    108.358 |     1.000 |

Tube Pressure Stress          |    219.436 |     1.000 |    141.727 |     1.000 |

---------------------------------------------------------------------------------

Minimum MAPnc                 |     38.329 |           |     38.329 |           |

(*) All load cases were analyzed to compute the MAWP for determining the test pressure.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Input Echo, Tubesheet Number     3,         Description: Tubesheet

Shell Data:

Main Shell Description: Port Barrel

Shell Maximum Design Pressure            Psd,max       28.60  bars

Shell Maximum Operating Pressure        Psox,max       28.60  bars

Shell Minimum Operating Pressure        Psox,min        0.00  bars

Shell Thickness                               ts     12.0000  mm.

Shell Internal Corrosion Allowance           cas      3.0000  mm.

Shell External Corrosion Allowance         caext      0.0000  mm.

Inside Diameter of Shell                      Ds     600.000  mm.

Shell Temperature for Internal Pressure       Ts       20.00  °C

Shell Material                                     SA-516 70

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Shell Material UNS Number                             K02700

Shell Allowable Stress at Temperature         Ss      137.90  N./mm²

Shell Allowable Stress at Ambient                     137.90  N./mm²

Channel Description: CH. Barrel

Channel Type:                                      Cylinder

Channel Maximum Design Pressure          Ptd,max        8.84  bars

Channel Maximum Operating Pressure      Ptox,max        8.84  bars

Channel Minimum Operating Pressure      Ptox,min        0.00  bars

Channel Thickness                             tc     10.0000  mm.

Channel Corrosion Allowance                  cac      3.0000  mm.

Inside Diameter of Channel                    Dc     600.000  mm.

Channel Design Temperature                 TEMPC       20.00  °C

Channel Material                                   SA-516 70

Note:

Using 2 * Yield for Discontinuity Stress Allowable (UG-23(e)), Sps.

Make sure that material properties at this temperature are not

time-dependent for Material: SA-516 70

Channel Material UNS Number                           K02700

Channel Allowable Stress at Temperature       Sc      137.90  N./mm²

Channel Allowable Stress at Ambient                   137.90  N./mm²

Tube Data:

Number of Tube Holes                          Nt         376

Tube Wall Thickness                           et      1.6500  mm.

Tube Outside Diameter                          D     19.0500  mm.

Total Straight Tube Length                    Lt     2500.00  mm.

Straight Tube Length (bet. inner tubsht faces) L     2440.00  mm.

Design Temperature of the Tubes                        20.00  °C

Tube Material                                       SA-334 6

Tube Material UNS Number                              K03006

Is this a Welded Tube                                     No

Tube Material Specification used           Smls. & wld. tube

Tube Allowable Stress at Temperature                  117.90  N./mm²

Tube Allowable Stress At Ambient                      117.90  N./mm²

Tube Yield Stress At design Temperature      Syt      241.32  N./mm²

Tube Pitch (Center to Center Spacing)          P     23.8130  mm.

Tube Layout Pattern                               Triangular

Radius to Outermost Tube Hole Center          ro     283.510  mm.

Largest Center-to-Center Tube Distance        Ul     52.3870  mm.

Length of Expanded Portion of Tube           ltx     57.0000  mm.

Tube-side pass partition groove depth         hg      5.0000  mm.

Tubesheet Data:

Tubesheet TYPE:  U-tube, Gasketed both Sides, Conf. d

Tubesheet Design Metal Temperature             T       20.00  °C

Tubesheet Material                                SA-350 LF2

Tubesheet Material UNS Number                         K03011

Tubesheet Allowable Stress at Temperature      S      223.40  N./mm²

Tubesheet Allowable Stress at Ambient         Tt      223.40  N./mm²

Thickness of Tubesheet                         h     60.0000  mm.

Tubesheet Corr. Allowance (Shell side)      Cats      3.0000  mm.

Tubesheet Corr. Allowance (Channel side)    Catc      3.0000  mm.

Tubesheet Outside Diameter                     A     650.000  mm.

Dimension G for the Channel Side              Gc     637.151  mm.

Area of the Untubed Lanes                     AL       425.5  cm²

Junction Stress Reduction option              Increase Tubesheet thickness

Perform Differential Pressure Design                      NO

Run Multiple Load Cases                                  YES

Additional Data for Gasketed Tubesheets:

Tubesheet Gasket on which Side                          Both

Flange Outside Diameter                        A     760.000  mm.

Flange Inside Diameter                         B     600.000  mm.

Flange Face Outside Diameter                 Fod     653.000  mm.

Flange Face Inside Diameter                  Fid     600.000  mm.

Gasket Outside Diameter                       Go     650.000  mm.

Gasket Inside Diameter                        Gi     624.000  mm.

Small end Hub thk.                            g0     12.0000  mm.

Large end Hub thk.                            g1     18.0000  mm.

Gasket Factor,                                 m        3.00

Gasket Design Seating Stress                   y       69.00  N./mm²

Flange Facing Sketch                          Code Sketch 1b

Column for Gasket Seating                     Code Column II

Gasket Thickness                              tg      4.5000  mm.

Full face Gasket Flange Option               Program Selects

Bolting Information:

Diameter of Bolt Circle                        C     705.000  mm.

Nominal Bolt Diameter                         dB     22.2250  mm.

Type of Thread Series                         TEMA Thread Series

Number of Bolts                                n          20

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature          Sb      172.38  N./mm²

Bolt Allowable Stress At Ambient              Sa      172.38  N./mm²

Weld between Flange and Shell/Channel                 0.0000  mm.

Alternate Flange Operating Bolt Load, Wm1           115486.97 Kgf

Alternate Flange Seating Bolt Load, Wm2              90480.76 Kgf

Alternate Flange Design Bolt Load, W                105258.09 Kgf

Tubesheet Integral with                                 None

Tubesheet Extended as Flange                              No

ASME TubeSheet Results per Part UHX, 2019

Elasticity/Expansion Material Properties :

Shell      - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature       20.0 °C      0.20277E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Channel    - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature       20.0 °C      0.20277E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Tubes      - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Tubsht. Design Temp.     20.0 °C      0.20277E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

TubeSheet  - TM-1     Carbon Steels with C<= 0.3%

-----------------------------------------------------------------

Elastic Mod. at Design Temperature       20.0 °C      0.20277E+09 KPa.

Elastic Mod. at Ambient Temperature      21.1 °C      0.20270E+09 KPa.

Tube Required Thickness under Internal Pressure (Tubeside pressure):

Thickness Due to Internal Pressure:

= (P*(D/2-CAE)) / (S*E+0.4*P) per Appendix 1-1 (a)(1)

= (8.84*(19/2-0)/(118*1+0.4*8.84)

= 0.0712 + 0.0000 = 0.0712 mm.

Tube Required Thickness under External Pressure (Shellside pressure) :

External Pressure Chart     CS-2             at        20.00  °C

Elastic Modulus for Material                    199943392.00  KPa.

Results for Max. Allowable External Pressure (Emawp):

TCA        ODCA     SLEN       D/T       L/D   Factor A        B

1.6500     19.05   2723.51     11.55   50.0000  0.0082522        122.73

EMAWP = (4*B)/(3*(D/T)) = ( 4 *123 )/( 3 *11.5 ) = 142 bars

Results for Reqd Thickness for Ext. Pressure (Tca):

TCA        ODCA     SLEN       D/T       L/D   Factor A        B

0.5187     19.05   2723.51     36.72   50.0000  0.0008156         78.79

EMAWP = (4*B)/(3*(D/T)) = ( 4 *78.8 )/( 3 *36.7 ) = 28.6 bars

Summary of Tube Required Thickness Results:

Total Required Thickness including Corrosion all.           0.5187  mm.

Allowable Internal Pressure at Corroded thickness           219.44  bars

Required Internal Design Pressure                             8.84  bars

Allowable External Pressure at Corroded thickness           141.73  bars

Required External Design Pressure                            28.60  bars

Required Thickness due to Shell Side pressure               0.5187  mm.

U-Tube Tubesheet results per ASME UHX-12 2019

Results for  6 Load Cases:

--Reqd. Thk. + CA       ---- Tubesheet  Stresses       Case    Pass/

Case#  Tbsht     Extnsn    Bend   Allwd    Shear  Allwd       Type    Fail

----------------------------------------------------------------------------

D1uc  31.295       0.772     103     447      11     132    Ps+Pt D1      Ok

D2uc  52.337       2.497     333     447      35     132    Ps+Pt D2      Ok

D3uc  44.306       1.725     230     447      24     132    Ps+Pt D3      Ok

D1c   34.274       0.772     114     447      12     132    Ps+Pt-c D1    Ok

D2c   55.295       2.497     369     447      39     132    Ps+Pt-c D2    Ok

D3c   47.324       1.725     255     447      27     132    Ps+Pt-c D3    Ok

----------------------------------------------------------------------------

Max:  55.2952       2.497  mm.      0.827           0.293  (Str. Ratio)

Load Case Definitions:

[Ps & Pt]:

Shell-side and Tube-side Design or Operating Pressures

derived from Psd,min Ptd,max, Psox,min, Ptox,max etc. per the

Load Case Tables

[c]:

With or Without Corrosion Allowance

[D1, D2, D3]:

Design Load Cases using the Maximum and Minimum Design Pressures

[D4]:

Design Load Case using the Minimum (Vacuum) Pressures (if specified)

Note:

Because there was no net pressure differential across the tubesheet due to

the specified pressures psd,min and ptd,min; load case D4 was not processed as

the resulting tubesheet bending stress would be zero.

Summary of Thickness Comparisons for  6 Load Cases:

Thickness (mm.)                         Required    Actual  P/F   |

------------------------------------------------------------------------------

Tubesheet Thickness :                               55.295     60.000   Ok   |

Tubesheet Thickness Flanged Extension :              2.497     50.000   Ok   |

Tube Thickness :                                     0.519      1.650   Ok   |

Tubesheet MAWP used to Compute Hydrotest Pressure:

Stress / Force           | Tubeside   |0 shellside| Shellside  |0 tubeside |

Condition              |    MAWP    |Stress Rat.|    MAWP    |Stress Rat.|

---------------------------------------------------------------------------------

Tubesheet Bending Stress      |     34.584 |     1.000 |     34.583 |     1.000 |

Tubesheet Shear Stress        |     97.515 |     1.000 |     97.515 |     1.000 |

Tube Pressure Stress          |    219.436 |     1.000 |    141.727 |     1.000 |

---------------------------------------------------------------------------------

Minimum MAWP                  |     34.584 |           |     34.583 |           |

Tubesheet MAPnc used to Compute Hydrotest Pressure:

Stress / Force           | Tubeside   |0 shellside| Shellside  |0 tubeside |

Condition              |    MAPnc   |Stress Rat.|    MAPnc   |Stress Rat.|

---------------------------------------------------------------------------------

Tubesheet Bending Stress      |     38.329 |     1.000 |     38.329 |     1.000 |

Tubesheet Shear Stress        |    108.358 |     1.000 |    108.358 |     1.000 |

Tube Pressure Stress          |    219.436 |     1.000 |    141.727 |     1.000 |

---------------------------------------------------------------------------------

Minimum MAPnc                 |     38.329 |           |     38.329 |           |

(*) All load cases were analyzed to compute the MAWP for determining the test pressure.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Flange Input Data Values                         Description: CH. FLANGE    :

CH. Flange

Description of Flange Geometry (Type)           Integral Weld Neck

Design Pressure                            P            8.89  bars

Design Temperature                                        20  °C

Internal Corrosion Allowance              ci          3.0000  mm.

External Corrosion Allowance              ce          0.0000  mm.

Use Corrosion Allowance in Thickness Calcs.              Yes

Flange Inside Diameter                     B         600.000  mm.

Flange Outside Diameter                    A         760.000  mm.

Flange Thickness                           t         60.0000  mm.

Thickness of Hub at Small End             go         10.0000  mm.

Thickness of Hub at Large End             g1         15.0000  mm.

Length of Hub                              h         25.0000  mm.

Flange Material                                     SA-266 2

Flange Material UNS number                            K03506

Flange Allowable Stress At Temperature   Sfo          223.40  N./mm²

Flange Allowable Stress At Ambient       Sfa          223.40  N./mm²

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature      Sb          210.00  N./mm²

Bolt Allowable Stress At Ambient          Sa          210.00  N./mm²

Diameter of Bolt Circle                    C         705.000  mm.

Nominal Bolt Diameter                      a         22.2250  mm.

Type of Threads                           TEMA Thread Series

Number of Bolts                                           20

Flange Face Outside Diameter             Fod         653.000  mm.

Flange Face Inside Diameter              Fid         600.000  mm.

Flange Facing Sketch                       2, Code Sketch 1b

Gasket Outside Diameter                   Go         650.000  mm.

Gasket Inside Diameter                    Gi         624.000  mm.

Gasket Factor                              m          3.0000

Gasket Design Seating Stress               y           69.00  N./mm²

Column for Gasket Seating                  2, Code Column II

Gasket Thickness                          tg          4.5000  mm.

Note:

The rigidity index calculation has been turned off. Please ensure the requirements

of 2-14(a) are met.

ASME Code, Section VIII Division 1, 2019

Hub Small End Required Thickness due to Internal Pressure:

= (P*(D/2+Ca))/(S*E-0.6*P) per UG-27 (c)(1)

= (8.89*(600/2+3))/(223*1-0.6*8.89)+Ca

= 4.2093 mm.

Hub Small End Hub MAWP:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (223 * 1 * 7 )/(303 + 0.6 * 7 )

= 50.902 bars

Corroded Flange Thickness, tc = T-ci                     57.000  mm.

Corroded Flange ID,      Bcor = B+2*Fcor                606.000  mm.

Corroded Large Hub,     g1Cor = g1-ci                    12.000  mm.

Corroded Small Hub,     g0Cor = go-ci                     7.000  mm.

Code R Dimension,           R = ((C-Bcor)/2)-g1cor       37.500  mm.

Gasket Contact Width,       N = (Go - Gi) / 2            13.000  mm.

Basic Gasket Width,        bo = N / 2                     6.500  mm.

Effective Gasket Width,     b = Cb sqrt(bo)               6.425  mm.

Gasket Reaction Diameter,   G = Go - 2 * b              637.151  mm.

Basic Flange and Bolt Loads:

Hydrostatic End Load due to Pressure [H]:

= 0.785 * G² * Peq

= 0.79 * 637² * 8.89

= 28918.035 Kgf

Contact Load on Gasket Surfaces [Hp]:

= 2 * b * Pi * G * m * P

= 2 * 6.42 * 3.14 * 637 * 3 * 8.89

= 6998.121 Kgf

Hydrostatic End Load at Flange ID [Hd]:

= Pi * Bcor² * P  / 4

= 3.14 * 606² *8.89/4

= 26159.504 Kgf

Pressure Force on Flange Face [Ht]:

= H - Hd

= 28918 - 26160

= 2758.531 Kgf

Operating Bolt Load [Wm1]:

= max( H + Hp + H'p, 0 )

= max( 28918 + 6998 + 0, 0 )

= 35916.156 Kgf

= 115620.258 Kgf, Mating Flange Load Governs

Gasket Seating Bolt Load [Wm2]:

= y * b * Pi * G  + yPart * bPart * lp

= 69*6.42*3.141*637+0*0*0

= 90480.758 Kgf

Required Bolt Area [Am]:

= Maximum of Wm1/Sb, Wm2/Sa

= Maximum of 115620/210, 90481/210

= 53.994 cm²

ASME Maximum Circumferential Spacing between Bolts per App. 2 eq. (3) [Bsmax]:

= 2a + 6t/(m + 0.5)

= 2 * 22.2 + 6 * 57/(3 + 0.5)

= 142.164 mm.

Actual Circumferential Bolt Spacing [Bs]:

= C * sin( pi / n )

= 705 * sin( 3.14/20 )

= 110.286 mm.

ASME Moment Multiplier for Bolt Spacing per App. 2 eq. (7) [Bsc]:

= max( sqrt( Bs/( 2a + t )), 1 )

= max( sqrt( 110/( 2 * 22.2 + 57 )), 1 )

= 1.0426

Bolting Information for TEMA Imperial Thread Series (Non Mandatory):

-------------------------------------------------------------------------

Minimum    Actual     Maximum

-------------------------------------------------------------------------

Bolt Area, cm²                              53.994     54.064

Radial Distance between Hub and Bolts:      31.750     37.500

Radial Distance between Bolts and Edge:     23.812     27.500

Circ. Spacing between the Bolts:            52.400    110.286    142.164

-------------------------------------------------------------------------

Min. Gasket Contact Width (Brownell Young) [Not an ASME Calc] [Nmin]:

= Ab * Sa/( y * Pi * (Go + Gi) )

= 54.1  * 210/(69 * 3.14 *(650 + 624 ) )

= 4.111 mm.

Flange Design Bolt Load, Gasket Seating [W]:

= Sa * ( Am + Ab ) / 2

= 210 *( 54 + 54.1 )/2

= 115695.93 Kgf

Gasket Load for the Operating Condition [HG]:

= Wm1 - H

= 115620 - 28918

= 86702.22 Kgf

Moment Arm Calculations:

Distance to Gasket Load Reaction [hg]:

= (C - G ) / 2

= ( 705 - 637 )/2

= 33.9246 mm.

Distance to Face Pressure Reaction [ht]:

= ( R + g1 + hg ) / 2

= ( 37.5 + 12 + 33.9 )/2

= 41.7123 mm.

Distance to End Pressure Reaction [hd]:

= R + ( g1 / 2 )

= 37.5 +( 12/2.0 )

= 43.5000 mm.

Summary of Moments for Internal Pressure: (Kg-m.)

Loading                 Force  |   Distance |  Bolt Corr |         Moment  |

----------------------------------------------------------------------------

End Pressure,   Md      26160. |    43.5000 |     1.0426 |           1186. |

Face Pressure,  Mt       2759. |    41.7123 |     1.0426 |            120. |

Gasket Load,    Mg      86702. |    33.9246 |     1.0426 |           3067. |

Gasket Seating, Matm   115696. |    33.9246 |     1.0426 |           4092. |

Total Moment for Operation,      Mop                                 4373. Kg-m.

Total Moment for Gasket seating, Matm                                4092. Kg-m.

Effective Hub Length, ho = sqrt(Bcor*goCor)           65.131  mm.

Hub Ratio,          h/h0 = HL / H0                     0.384

Thickness Ratio,   g1/g0 = (g1Cor/goCor)               1.714

Flange Factors for Integral Flange:

Factor F                                               0.858

Factor V                                               0.302

Factor f                                               1.217

Factors from Figure 2-7.1                     K =      1.254

T =      1.817            U =      9.566

Y =      8.705            Z =      4.491

d = 0.10120E+06 mm.³       e =     0.0132 mm.^-1

Stress Factors                            ALPHA =      1.751

BETA =      2.001        GAMMA =      0.964

DELTA =      1.830        Lamda =      2.794

Longitudinal Hub Stress, Operating [SHo]:

= ( f * Mop / Bcor ) / ( L * g1² )

= (1.22*4373/606)/(2.79*12²)

= 214.13 N./mm²

Longitudinal Hub Stress, Seating [SHa]:

= ( f * Matm / Bcor ) / ( L * g1² )

= (1.22*4092/606)/(2.79*12²)

= 200.38 N./mm²

Radial Flange Stress, Operating [SRo]:

= ( Beta * Mop / Bcor ) / ( L * t² )

= (2*4373/606)/(2.79*57²)

= 15.60 N./mm²

Radial Flange Stress, Seating [SRa]:

= ( Beta * Matm/Bcor ) / ( L * t² )

= (2*4092/606)/(2.79*57²)

= 14.60 N./mm²

Tangential Flange Stress, Operating [STo]:

= ( Y * Mo / (t² * Bcor) ) - Z * SRo

= (8.7*4373/(57²*606))-4.49*15.6

= 119.53 N./mm²

Tangential Flange Stress, Seating [STa]:

= ( y * Matm / (t² * Bcor) ) - Z * SRa

= (8.7*4092/(57²*606))-4.49*14.6

= 111.85 N./mm²

Average Flange Stress, Operating [SAo]:

= ( SHo + max( SRo, STo ) ) / 2

= (214+max(15.6,120))/2

= 166.83 N./mm²

Average Flange Stress, Seating [SAa]:

= ( SHa + max( SRa, STa ) ) / 2

= (200+max(14.6,112))/2

= 156.12 N./mm²

Bolt Stress, Operating [BSo]:

= Wm1 / Ab

= 115620/54.1

= 209.73 N./mm²

Bolt Stress, Seating [BSa]:

= ( Wm2 / Ab )

= (90481/54.1)

= 164.12 N./mm²

Flange Stress Analysis Results: N./mm²

Operating |            Gasket Seating |

Actual       Allowed |      Actual       Allowed |

-----------------------------------------------------------------------------

Longitudinal Hub           214.13 |      335.10 |      200.38 |      335.10 |

Radial Flange               15.60 |      223.40 |       14.60 |      223.40 |

Tangential Flange          119.53 |      223.40 |      111.85 |      223.40 |

Maximum Average            166.83 |      223.40 |      156.12 |      223.40 |

Bolting                    209.73 |      210.00 |      164.12 |      210.00 |

Minimum Required Flange Thickness                     51.892 mm.

Estimated M.A.W.P. ( Operating )                        28.7 bars

Estimated Finished Weight of Flange at given Thk.       84.1 kg.

Estimated Unfinished Weight of Forging at given Thk    112.6 kg.

Minimum Design Metal Temperature Results:

Thickness Ratio = 0.53, Temperature Reduction per Fig. UCS 66.1 = 29 °C

Min Metal Temp. w/o impact per UCS-66, Curve C             -44 °C

Min Metal Temp. at Required thickness (UCS 66.1)           -48 °C

Note: UCS-66(b)(-c) was considered in the flange MDMT calculation.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

Flange Input Data Values                         Description: SH. FLANGE    :

SH. Flange

Description of Flange Geometry (Type)           Integral Weld Neck

Design Pressure                            P           28.63  bars

Design Temperature                                        20  °C

Internal Corrosion Allowance              ci          3.0000  mm.

External Corrosion Allowance              ce          0.0000  mm.

Use Corrosion Allowance in Thickness Calcs.              Yes

Flange Inside Diameter                     B         600.000  mm.

Flange Outside Diameter                    A         760.000  mm.

Flange Thickness                           t         60.0000  mm.

Thickness of Hub at Small End             go         12.0000  mm.

Thickness of Hub at Large End             g1         18.0000  mm.

Length of Hub                              h         25.0000  mm.

Flange Material                                   SA-350 LF2

Flange Material UNS number                            K03011

Flange Allowable Stress At Temperature   Sfo          223.40  N./mm²

Flange Allowable Stress At Ambient       Sfa          223.40  N./mm²

Bolt Material                                      SA-193 B7

Bolt Allowable Stress At Temperature      Sb          210.00  N./mm²

Bolt Allowable Stress At Ambient          Sa          210.00  N./mm²

Diameter of Bolt Circle                    C         705.000  mm.

Nominal Bolt Diameter                      a         22.2250  mm.

Type of Threads                           TEMA Thread Series

Number of Bolts                                           20

Flange Face Outside Diameter             Fod         653.000  mm.

Flange Face Inside Diameter              Fid         600.000  mm.

Flange Facing Sketch                       2, Code Sketch 1b

Gasket Outside Diameter                   Go         650.000  mm.

Gasket Inside Diameter                    Gi         624.000  mm.

Gasket Factor                              m          3.0000

Gasket Design Seating Stress               y           69.00  N./mm²

Column for Gasket Seating                  2, Code Column II

Gasket Thickness                          tg          4.5000  mm.

Note:

The rigidity index calculation has been turned off. Please ensure the requirements

of 2-14(a) are met.

ASME Code, Section VIII Division 1, 2019

Hub Small End Required Thickness due to Internal Pressure:

= (P*(D/2+Ca))/(S*E-0.6*P) per UG-27 (c)(1)

= (28.6*(600/2+3))/(223*1-0.6*28.6)+Ca

= 6.9136 mm.

Hub Small End Hub MAWP:

= (S*E*t)/(R+0.6*t) per UG-27 (c)(1)

= (223 * 1 * 9 )/(303 + 0.6 * 9 )

= 65.191 bars

Corroded Flange Thickness, tc = T-ci                     57.000  mm.

Corroded Flange ID,      Bcor = B+2*Fcor                606.000  mm.

Corroded Large Hub,     g1Cor = g1-ci                    15.000  mm.

Corroded Small Hub,     g0Cor = go-ci                     9.000  mm.

Code R Dimension,           R = ((C-Bcor)/2)-g1cor       34.500  mm.

Gasket Contact Width,       N = (Go - Gi) / 2            13.000  mm.

Basic Gasket Width,        bo = N / 2                     6.500  mm.

Effective Gasket Width,     b = Cb sqrt(bo)               6.425  mm.

Gasket Reaction Diameter,   G = Go - 2 * b              637.151  mm.

Basic Flange and Bolt Loads:

Hydrostatic End Load due to Pressure [H]:

= 0.785 * G² * Peq

= 0.79 * 637² * 28.6

= 93092.109 Kgf

Contact Load on Gasket Surfaces [Hp]:

= 2 * b * Pi * G * m * P

= 2 * 6.42 * 3.14 * 637 * 3 * 28.6

= 22528.148 Kgf

Hydrostatic End Load at Flange ID [Hd]:

= Pi * Bcor² * P  / 4

= 3.14 * 606² *28.6/4

= 84211.922 Kgf

Pressure Force on Flange Face [Ht]:

= H - Hd

= 93092 - 84212

= 8880.184 Kgf

Operating Bolt Load [Wm1]:

= max( H + Hp + H'p, 0 )

= max( 93092 + 22528 + 0, 0 )

= 115620.258 Kgf

Gasket Seating Bolt Load [Wm2]:

= y * b * Pi * G  + yPart * bPart * lp

= 69*6.42*3.141*637+0*0*0

= 90480.758 Kgf

Required Bolt Area [Am]:

= Maximum of Wm1/Sb, Wm2/Sa

= Maximum of 115620/210, 90481/210

= 53.994 cm²

ASME Maximum Circumferential Spacing between Bolts per App. 2 eq. (3) [Bsmax]:

= 2a + 6t/(m + 0.5)

= 2 * 22.2 + 6 * 57/(3 + 0.5)

= 142.164 mm.

Actual Circumferential Bolt Spacing [Bs]:

= C * sin( pi / n )

= 705 * sin( 3.14/20 )

= 110.286 mm.

ASME Moment Multiplier for Bolt Spacing per App. 2 eq. (7) [Bsc]:

= max( sqrt( Bs/( 2a + t )), 1 )

= max( sqrt( 110/( 2 * 22.2 + 57 )), 1 )

= 1.0426

Bolting Information for TEMA Imperial Thread Series (Non Mandatory):

-------------------------------------------------------------------------

Minimum    Actual     Maximum

-------------------------------------------------------------------------

Bolt Area, cm²                              53.994     54.064

Radial Distance between Hub and Bolts:      31.750     34.500

Radial Distance between Bolts and Edge:     23.812     27.500

Circ. Spacing between the Bolts:            52.400    110.286    142.164

-------------------------------------------------------------------------

Min. Gasket Contact Width (Brownell Young) [Not an ASME Calc] [Nmin]:

= Ab * Sa/( y * Pi * (Go + Gi) )

= 54.1  * 210/(69 * 3.14 *(650 + 624 ) )

= 4.111 mm.

Flange Design Bolt Load, Gasket Seating [W]:

= Sa * ( Am + Ab ) / 2

= 210 *( 54 + 54.1 )/2

= 115695.93 Kgf

Gasket Load for the Operating Condition [HG]:

= Wm1 - H

= 115620 - 93092

= 22528.15 Kgf

Moment Arm Calculations:

Distance to Gasket Load Reaction [hg]:

= (C - G ) / 2

= ( 705 - 637 )/2

= 33.9246 mm.

Distance to Face Pressure Reaction [ht]:

= ( R + g1 + hg ) / 2

= ( 34.5 + 15 + 33.9 )/2

= 41.7123 mm.

Distance to End Pressure Reaction [hd]:

= R + ( g1 / 2 )

= 34.5 +( 15/2.0 )

= 42.0000 mm.

Summary of Moments for Internal Pressure: (Kg-m.)

Loading                 Force  |   Distance |  Bolt Corr |         Moment  |

----------------------------------------------------------------------------

End Pressure,   Md      84212. |    42.0000 |     1.0426 |           3688. |

Face Pressure,  Mt       8880. |    41.7123 |     1.0426 |            386. |

Gasket Load,    Mg      22528. |    33.9246 |     1.0426 |            797. |

Gasket Seating, Matm   115696. |    33.9246 |     1.0426 |           4092. |

Total Moment for Operation,      Mop                                 4871. Kg-m.

Total Moment for Gasket seating, Matm                                4092. Kg-m.

Effective Hub Length, ho = sqrt(Bcor*goCor)           73.851  mm.

Hub Ratio,          h/h0 = HL / H0                     0.339

Thickness Ratio,   g1/g0 = (g1Cor/goCor)               1.667

Flange Factors for Integral Flange:

Factor F                                               0.868

Factor V                                               0.326

Factor f                                               1.295

Factors from Figure 2-7.1                     K =      1.254

T =      1.817            U =      9.566

Y =      8.705            Z =      4.491

d = 0.17564E+06 mm.³       e =     0.0118 mm.^-1

Stress Factors                            ALPHA =      1.670

BETA =      1.893        GAMMA =      0.919

DELTA =      1.054        Lamda =      1.973

Longitudinal Hub Stress, Operating [SHo]:

= ( f * Mop / Bcor ) / ( L * g1² )

= (1.3*4871/606)/(1.97*15²)

= 229.96 N./mm²

Longitudinal Hub Stress, Seating [SHa]:

= ( f * Matm / Bcor ) / ( L * g1² )

= (1.3*4092/606)/(1.97*15²)

= 193.20 N./mm²

Radial Flange Stress, Operating [SRo]:

= ( Beta * Mop / Bcor ) / ( L * t² )

= (1.89*4871/606)/(1.97*57²)

= 23.27 N./mm²

Radial Flange Stress, Seating [SRa]:

= ( Beta * Matm/Bcor ) / ( L * t² )

= (1.89*4092/606)/(1.97*57²)

= 19.55 N./mm²

Tangential Flange Stress, Operating [STo]:

= ( Y * Mo / (t² * Bcor) ) - Z * SRo

= (8.7*4871/(57²*606))-4.49*23.3

= 106.66 N./mm²

Tangential Flange Stress, Seating [STa]:

= ( y * Matm / (t² * Bcor) ) - Z * SRa

= (8.7*4092/(57²*606))-4.49*19.6

= 89.61 N./mm²

Average Flange Stress, Operating [SAo]:

= ( SHo + max( SRo, STo ) ) / 2

= (230+max(23.3,107))/2

= 168.31 N./mm²

Average Flange Stress, Seating [SAa]:

= ( SHa + max( SRa, STa ) ) / 2

= (193+max(19.6,89.6))/2

= 141.41 N./mm²

Bolt Stress, Operating [BSo]:

= Wm1 / Ab

= 115620/54.1

= 209.73 N./mm²

Bolt Stress, Seating [BSa]:

= ( Wm2 / Ab )

= (90481/54.1)

= 164.12 N./mm²

Flange Stress Analysis Results: N./mm²

Operating |            Gasket Seating |

Actual       Allowed |      Actual       Allowed |

-----------------------------------------------------------------------------

Longitudinal Hub           229.96 |      335.10 |      193.20 |      335.10 |

Radial Flange               23.27 |      223.40 |       19.55 |      223.40 |

Tangential Flange          106.66 |      223.40 |       89.61 |      223.40 |

Maximum Average            168.31 |      223.40 |      141.41 |      223.40 |

Bolting                    209.73 |      210.00 |      164.12 |      210.00 |

Minimum Required Flange Thickness                     50.622 mm.

Estimated M.A.W.P. ( Operating )                        28.7 bars

Estimated Finished Weight of Flange at given Thk.       85.1 kg.

Estimated Unfinished Weight of Forging at given Thk    112.6 kg.

Minimum Design Metal Temperature Results:

Note:

This Material was specified as being an Impact Tested (Low Temperature) Material.

Impact Test Temperature provided per Specification         -46 °C

Note: UCS-66(b)(-c) was considered in the flange MDMT calculation.

PV Elite is a trademark of Hexagon AB, 2021, All rights reserved.

FEA for Nozzles T1 & T2 (3in.)

Tabular Results

Results were generated with the finite element program FE/Pipe®. Stress results are post-processed in accordance with the rules specified in ASME Section III and ASME Section VIII, Division 2.

Analysis Time Stamp: Wed Apr 17 11:30:56 2024.

- Model Notes

- Load Case Report

- Solution Data

- ASME Code Stress Output Plots

- Stress Results - Notes

- ASME Overstressed Areas

- Highest Primary Stress Ratios

- Highest Secondary Stress Ratios

- Highest Fatigue Stress Ratios

- Highest Stress Ratios Per Region

- Stress Intensification Factors

- Allowable Loads

- Compressive Stress Summary

- Flexibilities

- Graphical Results

Model Notes

Model Notes

Input Echo:

Model Type                    : Cylindrical Shell

Parent Geometry

Parent Outside Diam.   :     620.000 mm.

Thickness              :       7.000 mm.

Parent Properties:

Cold Allowable         :       137.9 MPa

Hot  Allowable         :       137.9 MPa

Material DB # 1016422.

Ultimate Tensile (Amb) :       482.6 MPa

Yield Strength (Amb)   :       262.0 MPa

Yield Strength (Hot)   :       242.0 MPa

Elastic Modulus (Amb)  :    202720.0 MPa

Poissons Ratio         :       0.300

Expansion Coefficient  :  0.1201E-04 mm./mm./deg.

Weight Density         :  0.0000E+00  N /cu.mm.(NOT USED)

Hillside Offset Distance      :     100.000 mm.

Nozzle Geometry

Nozzle Outside Diam.   :      88.900 mm.

Thickness              :       6.668 mm.

Length                 :     180.000 mm.

RePad Width            :      50.550 mm.

RePad Thickness        :      10.000 mm.

Nozzle Tilt Angle      :       0.000 deg.

Distance from Top      :       0.000 mm.

Distance from Bottom   :       0.000 mm.

Nozzle Properties

Cold Allowable         :       117.9 MPa

Hot  Allowable         :       117.9 MPa

Material DB # 1009922.

Ultimate Tensile (Amb) :       413.7 MPa

Yield Strength (Amb)   :       241.3 MPa

Yield Strength (Hot)   :       222.7 MPa

Elastic Modulus (Amb)  :    202720.0 MPa

Poissons Ratio         :       0.300

Expansion Coefficient  :  0.1201E-04 mm./mm./deg.

Weight Density         :  0.0000E+00  N /cu.mm. (NOT USED)

Design Operating Cycles       :          0.

Ambient Temperature (Deg.)    :       21.10

Uniform thermal expansion produces no stress in this geometry.

Any thermal loads will come through operating forces and

moments applied through the nozzle.

Nozzle Inside  Temperature    :       85.00 deg.

Nozzle Outside Temperature    :       85.00 deg.

Vessel Inside  Temperature    :       85.00 deg.

Vessel Outside Temperature    :       85.00 deg.

Nozzle Pressure               :       0.680 MPa

Vessel Pressure               :       0.680 MPa

Operating Pressure            :         0.7 MPa

The operating pressure is used for secondary and peak stress

cases. The design pressure is used for primary cases. The ratio

of the operating/design pressure = 1.000

User Defined Load Input Echo for the ATTACHMENT:

Loads are given at the Nozzle/Header Junction

Loads are defined in Global Coordinates

Forces(  N )  Moments (N-m)

Load Case        FX         FY         FZ         MX         MY         MZ

---------------------------------------------------------------------------

WEIGHT:    -3600.0     3600.0     2700.0      810.0      540.0      700.0

FEA Model Loads:

These are the actual Attachment loads applied to

the FEA model.

These are the User Defined Loads translated to the

end of the nozzle and reported in global coordinates.

Forces(  N )  Moments (N-m)

Load Case        FX         FY         FZ         MX         MY         MZ

---------------------------------------------------------------------------

WEIGHT:    -3600.0     3600.0     2700.0      324.0      540.0       52.0

The "top" or "positive" end of this model is "free" in

the axial and translational directions.

Stresses ARE nodally AVERAGED.

No weld dimensions have been given for the nozzle

connection to the shell. This will produce conservative

results for external loads and may tend to produce more

realistic inside surface pressure stresses.

No pad weld dimensions have been given for the pad

connection to the shell. Few correlations have been

performed to investigate the sensitivity of peak stresses

to this value. Reasonable lengths have been assumed.

The cylinder length or nozzle/branch location was adjusted

so that a better mesh could be generated at each end of the

cylinder. The nozzle is now located  311.15 mm.

down the length of the cylinder and the total cylinder length

is  622.30 mm.

Vessel Centerline  Vector     :  1.000   0.000   0.000

Nozzle Orientation Vector     :  0.000   1.000   0.000

Table of Contents

Load Case Report

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Load Case Report                                       $X

Inner and outer element temperatures are the same

throughout the model.  No thermal ratcheting

calculations will be performed.

THE   9  LOAD CASES ANALYZED ARE:

1   WEIGHT ONLY    (Wgt Only)

Weight ONLY case run to get the stress range

between the installed and the operating states.

/-------- Loads in Case   1

Loads due to Weight

2   SUSTAINED      (Wgt+Pr)

Sustained case run to satisfy local primary

membrane and bending stress limits.

/-------- Loads in Case   2

Loads due to Weight

Pressure Case    1

3   OPERATING

Case run to compute the operating stresses used in

secondary, peak and range calculations as needed.

/-------- Loads in Case   3

Pressure Case    1

Loads from (Operating)

4   RANGE          (Fatigue Calc Performed)

Case run to get the RANGE of stresses.

as described in NB-3222.2, 5.5.3.2, 5.5.5.2 or 5.5.6.1.

/-------- Combinations in Range Case   4

Plus  Stress Results from CASE   3

Minus Stress Results from CASE   1

5   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   5

Loads from (Axial)

6   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   6

Loads from (Inplane)

7   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   7

Loads from (Outplane)

8   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   8

Loads from (Torsion)

9   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   9

Pressure Case    1

Table of Contents

Solution Data

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Solution Data

Maximum Solution Row Size =     636

Number of Nodes           =    2652

Number of Elements        =     876

Number of Solution Cases  =       8

Summation of Loads per Case

Case #               FX                  FY                  FZ

1              -3600.               3600.               2700.

2             197092.               3038.               2700.

3             200692.               -562.                  0.

4                  0.             237524.                  0.

5                  3.                  0.                  1.

6                  0.                  0.                  3.

7                  0.                  0.                  0.

8             200692.               -562.                  0.

Table of Contents

ASME Code Stress Output Plots

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

ASME Code Stress Output Plots                          $X

1) Pl < SPL (SUS,Membrane) Case 2

2) Qb < SPS (SUS,Bending) Case 2

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

8) Membrane < User (OPE,Membrane) Case 3

9) Bending < User (OPE,Bending) Case 3

10) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 5

11) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 6

12) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 7

13) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 8

14) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 9

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Table of Contents

Stress Results - Notes

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Stress Results - Notes

- Results  in  this  analysis  were  generated using the finite

element solution method.

- Using 2019 ASME Section VIII Division 2

- Use Polished Bar fatigue curve.

- Ratio between Operating and Design Pressure =   1.000000

Range cases use operating pressure. Primary cases

use design pressure.

- Assume free end displacements of attached pipe

(e.g. thermal loads) are secondary loads.

- Primary bending stresses at discontinuities

are treated like secondary stresses. (Pb=0)

- Use Equivalent Stress (Von Mises).

- TRIAXIAL Stress Guidelines:

S1+S2+S3 evaluation omitted from operating stress.

Include S1+S2+S3 evaluation in primary case evaluation.

Bending stress NOT included for all S1+S2+S3 calculations.

- Use local tensor values for averaged and not averaged stresses.

Table of Contents

ASME Overstressed Areas

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

ASME Overstressed Areas                                $X

*** NO OVERSTRESSED NODES IN THIS MODEL ***

Table of Contents

Highest Primary Stress Ratios

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Highest Primary Stress Ratios                          $X

Header/Pad at Junction

Pl            SPL     Primary Membrane Load Case 2

42            242     Min Prin. Stress = -31. (67% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

17%

Branch at Junction

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

168            464     Min Prin. Stress = -119. (82% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

36%

Branch Transition

Pl            SPL     Primary Membrane Load Case 2

30            223     Min Prin. Stress = -26. (97% Neg, 78% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

13%

Pad Outer Edge Weld

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

116            504     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

23%

Header/Pad removed from Junction

Pl            SPL     Primary Membrane Load Case 2

33            242     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

13%

Branch removed from Junction

Pl            SPL     Primary Membrane Load Case 2

32            223     Min Prin. Stress = -30. (94% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

14%

Table of Contents

Highest Secondary Stress Ratios

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Highest Secondary Stress Ratios                        $X

In combination case  4 the max range stress divided

by the max component stress is 1.98. The case tensor components

are in some directions additive and so the combination

case will have HIGHER stresses than the largest of any

of the individual cases by more than 50%.

Load      Combined/Max       Combined/Max

Case        (Inside)           (Outside)

------    -------------      -------------

4         1.968               1.983

Header/Pad at Junction

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

85            504     Min Prin. Stress = -43. (81% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

16%

Branch at Junction

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

201            464     Min Prin. Stress = -145. (85% Neg, 29% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

43%

Branch Transition

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

36            464     Min Prin. Stress = -30. (88% Neg, 66% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

7%

Pad Outer Edge Weld

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

116            504     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

23%

Header/Pad removed from Junction

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

46            504     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

9%

Branch removed from Junction

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

46            464     Min Prin. Stress = -42. (91% Neg, 58% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

10%

Table of Contents

Highest Fatigue Stress Ratios

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Highest Fatigue Stress Ratios                          $X

Header/Pad at Junction

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

115     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.005 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 2.2279E9

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 7,592,540.

WRC 474 99% Probability Cycles = 1,763,816.

0%                    WRC 474 95% Probability Cycles = 2,448,836.

BS5500 Allowed Cycles(Curve F) = 1,126,150.

Membrane-to-Bending Ratio = 0.459

Bending-to-PL+PB+Q Ratio = 0.685

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Branch at Junction

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

271     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.011 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 98,775.

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1,033,402.

WRC 474 99% Probability Cycles = 240,069.

1%                    WRC 474 95% Probability Cycles = 333,305.

BS5500 Allowed Cycles(Curve F) = 85,077.

Membrane-to-Bending Ratio = 0.325

Bending-to-PL+PB+Q Ratio = 0.755

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch Transition

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

36     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.001 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.9594E8

WRC 474 99% Probability Cycles = 45,519,084.

0%                    WRC 474 95% Probability Cycles = 63,197,524.

BS5500 Allowed Cycles(Curve F) = 20,613,216.

Membrane-to-Bending Ratio = 9.953

Bending-to-PL+PB+Q Ratio = 0.091

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Pad Outer Edge Weld

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

146     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.006 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 16,071,699.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 6,451,036.

WRC 474 99% Probability Cycles = 1,498,634.

0%                    WRC 474 95% Probability Cycles = 2,080,665.

BS5500 Allowed Cycles(Curve F) = 540,636.

Membrane-to-Bending Ratio = 0.519

Bending-to-PL+PB+Q Ratio = 0.658

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Header/Pad removed from Junction

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

42     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.1606E8

WRC 474 99% Probability Cycles = 26,961,756.

0%                    WRC 474 95% Probability Cycles = 37,433,004.

BS5500 Allowed Cycles(Curve F) = 9,328,373.

Membrane-to-Bending Ratio = 1.864

Bending-to-PL+PB+Q Ratio = 0.349

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch removed from Junction

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

46     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 86,172,024.

WRC 474 99% Probability Cycles = 20,018,544.

0%                    WRC 474 95% Probability Cycles = 27,793,228.

BS5500 Allowed Cycles(Curve F) = 6,881,620.

Membrane-to-Bending Ratio = 3.189

Bending-to-PL+PB+Q Ratio = 0.239

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Table of Contents

Highest Stress Ratios Per Region

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Highest Stress Ratios Per Region                       $X

Header/Pad at Junction

Pl            SPL     Primary Membrane Load Case 2

42            242     Min Prin. Stress = -31. (67% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

17%

Qb            SPS     Primary Bending Load Case 2

65            504     Min Prin. Stress = -31. (67% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

12%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

75            504     Min Prin. Stress = -31. (67% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

14%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

61            504     Min Prin. Stress = -31. (67% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

12%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

42            552     Min Prin. Stress = -31. (67% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

7%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

41            504     Min Prin. Stress = -7. (29% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

8%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

13            504     Min Prin. Stress = -7. (29% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

2%

Membrane           User     Component Evaluation Load Case 3

24            504     Min Prin. Stress = -7. (29% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

4%

Bending           User     Component Evaluation Load Case 3

19            504     Min Prin. Stress = -7. (29% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

3%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

85            504     Min Prin. Stress = -43. (81% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

16%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

64            504     Min Prin. Stress = -43. (81% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

12%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

115     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.005 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 2.2279E9

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 7,592,540.

WRC 474 99% Probability Cycles = 1,763,816.

0%                    WRC 474 95% Probability Cycles = 2,448,836.

BS5500 Allowed Cycles(Curve F) = 1,126,150.

Membrane-to-Bending Ratio = 0.459

Bending-to-PL+PB+Q Ratio = 0.685

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

86     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.003 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 21,273,600.

WRC 474 99% Probability Cycles = 4,942,045.

0%                    WRC 474 95% Probability Cycles = 6,861,408.

BS5500 Allowed Cycles(Curve F) = 2,635,012.

Membrane-to-Bending Ratio = 0.330

Bending-to-PL+PB+Q Ratio = 0.752

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch at Junction

Pl            SPL     Primary Membrane Load Case 2

55            223     Min Prin. Stress = -119. (82% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

24%

Qb            SPS     Primary Bending Load Case 2

151            464     Min Prin. Stress = -119. (82% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

32%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

148            464     Min Prin. Stress = -119. (82% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

31%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

168            464     Min Prin. Stress = -119. (82% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

36%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

83            472     Min Prin. Stress = -119. (82% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

17%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

33            464     Min Prin. Stress = -24. (63% Neg, 11% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

7%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

39            464     Min Prin. Stress = -24. (63% Neg, 11% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

8%

Membrane           User     Component Evaluation Load Case 3

14            464     Min Prin. Stress = -24. (63% Neg, 11% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

2%

Bending           User     Component Evaluation Load Case 3

35            464     Min Prin. Stress = -24. (63% Neg, 11% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

7%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

154            464     Min Prin. Stress = -145. (85% Neg, 29% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

33%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

201            464     Min Prin. Stress = -145. (85% Neg, 29% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

43%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

208     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.008 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 276,618.

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 2,804,450.

WRC 474 99% Probability Cycles = 651,499.

0%                    WRC 474 95% Probability Cycles = 904,525.

BS5500 Allowed Cycles(Curve F) = 188,899.

Membrane-to-Bending Ratio = 0.307

Bending-to-PL+PB+Q Ratio = 0.765

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

271     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.011 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 98,775.

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1,033,402.

WRC 474 99% Probability Cycles = 240,069.

1%                    WRC 474 95% Probability Cycles = 333,305.

BS5500 Allowed Cycles(Curve F) = 85,077.

Membrane-to-Bending Ratio = 0.325

Bending-to-PL+PB+Q Ratio = 0.755

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch Transition

Pl            SPL     Primary Membrane Load Case 2

30            223     Min Prin. Stress = -26. (97% Neg, 78% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

13%

Qb            SPS     Primary Bending Load Case 2

9            464     Min Prin. Stress = -26. (97% Neg, 78% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

1%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

32            464     Min Prin. Stress = -26. (97% Neg, 78% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

6%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

32            464     Min Prin. Stress = -26. (97% Neg, 78% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

6%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

30            472     Min Prin. Stress = -26. (97% Neg, 78% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

6%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

8            464     Min Prin. Stress = -3. (57% Neg, 37% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

1%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

7            464     Min Prin. Stress = -3. (57% Neg, 37% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

1%

Membrane           User     Component Evaluation Load Case 3

7            464     Min Prin. Stress = -3. (57% Neg, 37% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

1%

Bending           User     Component Evaluation Load Case 3

6            464     Min Prin. Stress = -3. (57% Neg, 37% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

1%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

31            464     Min Prin. Stress = -30. (88% Neg, 66% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

6%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

36            464     Min Prin. Stress = -30. (88% Neg, 66% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

7%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

31     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.001 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 3.0174E8

WRC 474 99% Probability Cycles = 70,096,664.

0%                    WRC 474 95% Probability Cycles = 97,320,392.

BS5500 Allowed Cycles(Curve F) = 41,067,668.

Membrane-to-Bending Ratio = 9.579

Bending-to-PL+PB+Q Ratio = 0.095

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

36     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.001 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.9594E8

WRC 474 99% Probability Cycles = 45,519,084.

0%                    WRC 474 95% Probability Cycles = 63,197,524.

BS5500 Allowed Cycles(Curve F) = 20,613,216.

Membrane-to-Bending Ratio = 9.953

Bending-to-PL+PB+Q Ratio = 0.091

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Pad Outer Edge Weld

Pl            SPL     Primary Membrane Load Case 2

41            242     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

17%

Qb            SPS     Primary Bending Load Case 2

81            504     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

16%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

54            504     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

10%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

116            504     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

23%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

65            552     Min Prin. Stress = -10. (22% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

11%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

32            504     Min Prin. Stress = -4. ( 6% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

6%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

50            504     Min Prin. Stress = -4. ( 6% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

10%

Membrane           User     Component Evaluation Load Case 3

27            504     Min Prin. Stress = -4. ( 6% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

5%

Bending           User     Component Evaluation Load Case 3

26            504     Min Prin. Stress = -4. ( 6% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

5%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

56            504     Min Prin. Stress = -12. (41% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

11%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

109            504     Min Prin. Stress = -12. (41% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

21%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

75     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.003 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 48,120,244.

WRC 474 99% Probability Cycles = 11,178,770.

0%                    WRC 474 95% Probability Cycles = 15,520,316.

BS5500 Allowed Cycles(Curve F) = 3,994,395.

Membrane-to-Bending Ratio = 1.610

Bending-to-PL+PB+Q Ratio = 0.383

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

146     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.006 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 16,071,699.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 6,451,036.

WRC 474 99% Probability Cycles = 1,498,634.

0%                    WRC 474 95% Probability Cycles = 2,080,665.

BS5500 Allowed Cycles(Curve F) = 540,636.

Membrane-to-Bending Ratio = 0.519

Bending-to-PL+PB+Q Ratio = 0.658

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Header/Pad removed from Junction

Pl            SPL     Primary Membrane Load Case 2

33            242     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

13%

Qb            SPS     Primary Bending Load Case 2

18            504     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

3%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

46            504     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

9%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

39            504     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

7%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

54            552     Min Prin. Stress = -5. (25% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

9%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

31            504     Min Prin. Stress = -2. (23% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

6%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

34            504     Min Prin. Stress = -2. (23% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

6%

Membrane           User     Component Evaluation Load Case 3

28            504     Min Prin. Stress = -2. (23% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

5%

Bending           User     Component Evaluation Load Case 3

8            504     Min Prin. Stress = -2. (23% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

1%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

42            504     Min Prin. Stress = -2. (23% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

8%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

42            504     Min Prin. Stress = -2. (23% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

8%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

42     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.1774E8

WRC 474 99% Probability Cycles = 27,351,872.

0%                    WRC 474 95% Probability Cycles = 37,974,628.

BS5500 Allowed Cycles(Curve F) = 9,493,398.

Membrane-to-Bending Ratio = 1.954

Bending-to-PL+PB+Q Ratio = 0.339

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

42     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.1606E8

WRC 474 99% Probability Cycles = 26,961,756.

0%                    WRC 474 95% Probability Cycles = 37,433,004.

BS5500 Allowed Cycles(Curve F) = 9,328,373.

Membrane-to-Bending Ratio = 1.864

Bending-to-PL+PB+Q Ratio = 0.349

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch removed from Junction

Pl            SPL     Primary Membrane Load Case 2

32            223     Min Prin. Stress = -30. (94% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

14%

Qb            SPS     Primary Bending Load Case 2

11            464     Min Prin. Stress = -30. (94% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

2%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

40            464     Min Prin. Stress = -30. (94% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

8%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

32            464     Min Prin. Stress = -30. (94% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

6%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

47            472     Min Prin. Stress = -30. (94% Neg, 40% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

9%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

8            464     Min Prin. Stress = -6. (66% Neg, 8% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

1%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

8            464     Min Prin. Stress = -6. (66% Neg, 8% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

1%

Membrane           User     Component Evaluation Load Case 3

7            464     Min Prin. Stress = -6. (66% Neg, 8% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

1%

Bending           User     Component Evaluation Load Case 3

2            464     Min Prin. Stress = -6. (66% Neg, 8% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

0%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

46            464     Min Prin. Stress = -42. (91% Neg, 58% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

10%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

37            464     Min Prin. Stress = -42. (91% Neg, 58% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

8%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

46     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 86,172,024.

WRC 474 99% Probability Cycles = 20,018,544.

0%                    WRC 474 95% Probability Cycles = 27,793,228.

BS5500 Allowed Cycles(Curve F) = 6,881,620.

Membrane-to-Bending Ratio = 3.189

Bending-to-PL+PB+Q Ratio = 0.239

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

37     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.001 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.7048E8

WRC 474 99% Probability Cycles = 39,603,136.

0%                    WRC 474 95% Probability Cycles = 54,983,972.

BS5500 Allowed Cycles(Curve F) = 16,564,323.

Membrane-to-Bending Ratio = 25.559

Bending-to-PL+PB+Q Ratio = 0.038

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Table of Contents

Stress Intensification Factors

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Stress Intensification Factors                         $X

Branch/Nozzle Sif Summary

Peak      Primary    Secondary      SSI

Axial   :        6.168       4.569       9.137       1.520

Inplane :        2.465       1.826       3.652       1.350

Outplane:        3.291       2.438       4.875       1.315

Torsion :        1.064       1.060       1.576       1.032

Pressure:        1.130       0.920       1.674       1.029

The above stress intensification factors are to be used

in a beam-type analysis of the piping system.  Inplane,

Outplane and Torsional sif's should be used with the

matching branch pipe whose diameter and thickness is given

below.  The axial sif should be used to intensify the

axial stress in the branch pipe calculated by F/A.  The

pressure sif should be used to intensify the nominal

pressure stress in the PARENT or HEADER, calculated

from PDo/2T. B31 calculations use mean diameters and

Section VIII calculations use outside diameters. SSIs are

based on peak stress factors and correlated test results.

Pipe OD :       88.900  mm.

Pipe Thk:        6.668  mm.

Z approx:    35411.109  cu.mm.

Z exact :    32970.617  cu.mm.

(SSI = SIF^x)        Axial   Inpl    Outpl   Tors    Pres

SIF/SSI Exponents:     0.835   0.667   0.748   0.939  -0.679

SIF/SSI exponent based on relationship between primary and

peak stress factors from the finite element analysis.

B31.3 Branch Pressure i-factor =       16.232

Header Pressure i-factor =        2.286

The B31.3 pressure i-factors should be used with with

F/A, where F is the axial force due to pressure, and

A is the area of the pipe wall. This is equivalent to

finding the pressure stress from (ip)(PD/4T).

B31.3   (Branch)

Peak Stress Sif ....    0.000         Axial

3.491         Inplane

4.337         Outplane

1.000         Torsional

B31.1  (Branch)

Peak Stress Sif ....    0.000         Axial

4.337         Inplane

4.337         Outplane

4.337         Torsional

WRC 330  (Branch)

Peak Stress Sif ....    0.000         Axial

4.553         Inplane

4.337         Outplane

4.553         Torsional

Table of Contents

Allowable Loads

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Allowable Loads                                        $X

SECONDARY                     Maximum     Conservative         Realistic

Load Type (Range):         Individual     Simultaneous        Simultaneous

Occuring       Occuring            Occuring

Axial Force      ( N     )      87471.        26719.              40079.

Inplane   Moment (mm.  N )    4188848.       904774.            1919316.

Outplane  Moment (mm.  N )    3138085.       677814.            1437860.

Torsional Moment (mm.  N )    9704841.      2964484.            4446726.

Pressure         (MPa    )       6.80          0.68                0.68

PRIMARY                       Maximum     Conservative         Realistic

Load Type:                 Individual     Simultaneous        Simultaneous

Occuring       Occuring            Occuring

Axial Force      ( N     )      83965.        25550.              38326.

Inplane   Moment (mm.  N )    4020933.       865196.            1835359.

Outplane  Moment (mm.  N )    3012291.       648164.            1374963.

Torsional Moment (mm.  N )    6926760.      2107817.            3161726.

Pressure         (MPa    )       5.94          0.68                0.68

NOTES:

1) Maximum Individual Occuring Loads are the maximum

allowed values of the respective loads if all other

load components are zero, i.e. the listed axial force

may be applied if the inplane, outplane and torsional

moments, and the pressure are zero.

2) The Conservative Allowable Simultaneous loads are

the maximum loads that can be applied simultaneously.

A conservative stress combination equation is used

that typically produces stresses within 50-70% of the

allowable stress.

3) The Realistic Allowable Simultaneous loads are the

maximum loads that can be applied simultaneously.  A

more realistic stress combination equation is used

based on experience at Paulin Research.  Stresses are

typically produced within 80-105% of the allowable.

4) Secondary allowable loads are limits for expansion

and operating piping loads.

5) Primary allowable loads are limits for weight,

primary and sustained type piping loads.

6) High D/T low pressure systems may be subject to

instability and should be checked when compressive

stresses are present.

Table of Contents

Compressive Stress Summary

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Compressive Stress Summary (MPa)                       $X

Nomenclature:

-------------

Min Stress       - Compressive Membrane and Bending Stress

Pts in Region    - No. of nodes in the model region

>5% Compression  - 5% or more of Compressive Stress Limit

>50% Compression - 50% or more of Compressive Stress Limit

Compressive Stress Limit = -0.55 Min(Sy, kEt/R), Section

slenderness ratio (elastic buckling) not considered.

>5%    >50%

Min        Pts      Compression

#  Load Type  Case    Stress    in Region   and Bending    Region

--  ---------  ----    ------   ----------  ------------  ----------------

1  SUSTAINED    2        -10.      1272      22%     0%  Pad Outer Edge Weld

2  OPERATING    3         -4.      1272       6%     0%  Pad Outer Edge Weld

3  EXPANSION    4        -12.      1272      41%     0%  Pad Outer Edge Weld

4  SUSTAINED    2         -5.       648      25%     0%  Header/Pad removed from Junction

5  OPERATING    3         -2.       648      23%     0%  Header/Pad removed from Junction

6  EXPANSION    4         -2.       648      23%     0%  Header/Pad removed from Junction

7  SUSTAINED    2       -119.       960      82%    40%  Branch at Junction

8  OPERATING    3        -24.       960      63%    11%  Branch at Junction

9  EXPANSION    4       -145.       960      85%    29%  Branch at Junction

10  SUSTAINED    2        -30.       432      94%    40%  Branch removed from Junction

11  OPERATING    3         -6.       432      66%     8%  Branch removed from Junction

12  EXPANSION    4        -42.       432      91%    58%  Branch removed from Junction

13  SUSTAINED    2        -26.      1104      97%    78%  Branch Transition

14  OPERATING    3         -3.      1104      57%    37%  Branch Transition

15  EXPANSION    4        -30.      1104      88%    66%  Branch Transition

16  SUSTAINED    2        -31.       576      67%     0%  Header/Pad at Junction

17  OPERATING    3         -7.       576      29%     0%  Header/Pad at Junction

18  EXPANSION    4        -43.       576      81%     0%  Header/Pad at Junction

Table of Contents

Flexibilities

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:30am  APR 17,2024

Flexibilities                                          $X

The following stiffnesses should be used in a piping,

"beam-type" analysis of the intersection.  The stiff-

nesses should be inserted at the surface of the

branch/header or nozzle/vessel junction.  The general

characteristics used for the branch pipe should be:

Outside Diameter =   88.900  mm.

Wall Thickness   =    6.668  mm.

Axial Translational Stiffness   =        162521.   N /mm.

Inplane Rotational Stiffness    =      18359652.  mm. N /deg

Outplane Rotational Stiffness   =       8047242.  mm. N /deg

Torsional Rotational Stiffness  =     145807360.  mm. N /deg

Estimated Radial Shell Displacement due to Allowable Loads

SECONDARY:

Axial (mm.) =  0.538  In-Plane (mm.) =  0.164  Out-Plane (mm.) =  0.280

PRIMARY

Axial (mm.) =  0.517  In-Plane (mm.) =  0.157  Out-Plane (mm.) =  0.269

Secondary Conservative Displacement =  0.260 mm.

Secondary Realistic    Displacement =  0.450 mm.

Primary Conservative Displacement =  0.249 mm.

Primary Realistic Displacement    =  0.430 mm.

Intersection Flexibility Factors for Branch/Nozzle                                                                   :

Find axial stiffness: K = 3EI/(kd)^3   N /mm.

Find bending and torsional stiffnesses: K = EI/(kd)  mm. N per radian.

The EI product is   0.29751E+12    N mm.^2

The value of (d) to use is:  82.232  mm..

The resulting bending stiffness is in units of force x length per radian.

Axial Flexibility Factor     (k) =     2.145

Inplane Flexibility Factor   (k) =     3.439

Outplane Flexibility Factor  (k) =     7.847

Torsional Flexibility Factor (k) =     0.433

Table of Contents

FEA for Nozzle S1 (4in.)

Tabular Results

Results were generated with the finite element program FE/Pipe®. Stress results are post-processed in accordance with the rules specified in ASME Section III and ASME Section VIII, Division 2.

Analysis Time Stamp: Wed Apr 17 11:34:19 2024.

- Model Notes

- Load Case Report

- Solution Data

- ASME Code Stress Output Plots

- Stress Results - Notes

- ASME Overstressed Areas

- Highest Primary Stress Ratios

- Highest Secondary Stress Ratios

- Highest Fatigue Stress Ratios

- Highest Stress Ratios Per Region

- Stress Intensification Factors

- Allowable Loads

- Compressive Stress Summary

- Flexibilities

- Graphical Results

Model Notes

Model Notes

Input Echo:

Model Type                    : Cylindrical Shell

Parent Geometry

Parent Outside Diam.   :     712.000 mm.

Thickness              :       9.000 mm.

Parent Properties:

Cold Allowable         :       137.9 MPa

Hot  Allowable         :       137.9 MPa

Material DB # 1016422.

Ultimate Tensile (Amb) :       482.6 MPa

Yield Strength (Amb)   :       262.0 MPa

Yield Strength (Hot)   :       235.8 MPa

Elastic Modulus (Amb)  :    202720.0 MPa

Poissons Ratio         :       0.300

Expansion Coefficient  :  0.1223E-04 mm./mm./deg.

Weight Density         :  0.0000E+00  N /cu.mm.(NOT USED)

Nozzle Geometry

Nozzle Outside Diam.   :     114.300 mm.

Thickness              :       9.735 mm.

Length                 :     150.000 mm.

RePad Width            :      52.850 mm.

RePad Thickness        :      12.000 mm.

Nozzle Tilt Angle      :       0.000 deg.

Distance from Top      :       0.000 mm.

Distance from Bottom   :       0.000 mm.

Nozzle Properties

Cold Allowable         :       117.9 MPa

Hot  Allowable         :       117.9 MPa

Material DB # 1010222.

Ultimate Tensile (Amb) :       413.7 MPa

Yield Strength (Amb)   :       241.3 MPa

Yield Strength (Hot)   :       217.2 MPa

Elastic Modulus (Amb)  :    202720.0 MPa

Poissons Ratio         :       0.300

Expansion Coefficient  :  0.1223E-04 mm./mm./deg.

Weight Density         :  0.0000E+00  N /cu.mm. (NOT USED)

Design Operating Cycles       :          0.

Ambient Temperature (Deg.)    :       21.10

Uniform thermal expansion produces no stress in this geometry.

Any thermal loads will come through operating forces and

moments applied through the nozzle.

Nozzle Inside  Temperature    :      120.00 deg.

Nozzle Outside Temperature    :      120.00 deg.

Vessel Inside  Temperature    :      120.00 deg.

Vessel Outside Temperature    :      120.00 deg.

Nozzle Pressure               :       2.200 MPa

Vessel Pressure               :       2.200 MPa

Operating Pressure            :         2.2 MPa

The operating pressure is used for secondary and peak stress

cases. The design pressure is used for primary cases. The ratio

of the operating/design pressure = 1.000

User Defined Load Input Echo for the ATTACHMENT:

Loads are given at the Nozzle/Header Junction

Loads are defined in Global Coordinates

Forces(  N )  Moments (N-m)

Load Case        FX         FY         FZ         MX         MY         MZ

---------------------------------------------------------------------------

WEIGHT:    -5600.0     5600.0     4200.0     1680.0     1120.0     1460.0

FEA Model Loads:

These are the actual Attachment loads applied to

the FEA model.

These are the User Defined Loads translated to the

end of the nozzle and reported in global coordinates.

Forces(  N )  Moments (N-m)

Load Case        FX         FY         FZ         MX         MY         MZ

---------------------------------------------------------------------------

WEIGHT:    -5600.0     5600.0     4200.0     1050.0     1120.0      620.0

The "top" or "positive" end of this model is "free" in

the axial and translational directions.

Stresses ARE nodally AVERAGED.

No weld dimensions have been given for the nozzle

connection to the shell. This will produce conservative

results for external loads and may tend to produce more

realistic inside surface pressure stresses.

No pad weld dimensions have been given for the pad

connection to the shell. Few correlations have been

performed to investigate the sensitivity of peak stresses

to this value. Reasonable lengths have been assumed.

The cylinder length or nozzle/branch location was adjusted

so that a better mesh could be generated at each end of the

cylinder. The nozzle is now located  400.05 mm.

down the length of the cylinder and the total cylinder length

is  800.10 mm.

Vessel Centerline  Vector     :  1.000   0.000   0.000

Nozzle Orientation Vector     :  0.000   1.000   0.000

Table of Contents

Load Case Report

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Load Case Report                                       $X

Inner and outer element temperatures are the same

throughout the model.  No thermal ratcheting

calculations will be performed.

THE   9  LOAD CASES ANALYZED ARE:

1   WEIGHT ONLY    (Wgt Only)

Weight ONLY case run to get the stress range

between the installed and the operating states.

/-------- Loads in Case   1

Loads due to Weight

2   SUSTAINED      (Wgt+Pr)

Sustained case run to satisfy local primary

membrane and bending stress limits.

/-------- Loads in Case   2

Loads due to Weight

Pressure Case    1

3   OPERATING

Case run to compute the operating stresses used in

secondary, peak and range calculations as needed.

/-------- Loads in Case   3

Pressure Case    1

Loads from (Operating)

4   RANGE          (Fatigue Calc Performed)

Case run to get the RANGE of stresses.

as described in NB-3222.2, 5.5.3.2, 5.5.5.2 or 5.5.6.1.

/-------- Combinations in Range Case   4

Plus  Stress Results from CASE   3

Minus Stress Results from CASE   1

5   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   5

Loads from (Axial)

6   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   6

Loads from (Inplane)

7   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   7

Loads from (Outplane)

8   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   8

Loads from (Torsion)

9   Program Generated -- Force Only

Case run to compute sif's and flexibilities.

/-------- Loads in Case   9

Pressure Case    1

Table of Contents

Solution Data

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Solution Data

Maximum Solution Row Size =     690

Number of Nodes           =    2184

Number of Elements        =     720

Number of Solution Cases  =       8

Summation of Loads per Case

Case #               FX                  FY                  FZ

1              -5600.               5600.               4200.

2             848303.               2246.               4200.

3             853903.              -3354.                  0.

4                  0.             440969.                  0.

5                  0.                  0.                  0.

6                  0.                  0.                  0.

7                  0.                  0.                  0.

8             853903.              -3354.                  0.

Table of Contents

ASME Code Stress Output Plots

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

ASME Code Stress Output Plots                          $X

1) Pl < SPL (SUS,Membrane) Case 2

2) Qb < SPS (SUS,Bending) Case 2

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

8) Membrane < User (OPE,Membrane) Case 3

9) Bending < User (OPE,Bending) Case 3

10) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 5

11) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 6

12) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 7

13) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 8

14) Pl+Pb+Q+F < 2Sa (SIF,Outside) Case 9

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Table of Contents

Stress Results - Notes

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Stress Results - Notes

- Results  in  this  analysis  were  generated using the finite

element solution method.

- Using 2019 ASME Section VIII Division 2

- Use Polished Bar fatigue curve.

- Ratio between Operating and Design Pressure =   1.000000

Range cases use operating pressure. Primary cases

use design pressure.

- Assume free end displacements of attached pipe

(e.g. thermal loads) are secondary loads.

- Primary bending stresses at discontinuities

are treated like secondary stresses. (Pb=0)

- Use Equivalent Stress (Von Mises).

- TRIAXIAL Stress Guidelines:

S1+S2+S3 evaluation omitted from operating stress.

Include S1+S2+S3 evaluation in primary case evaluation.

Bending stress NOT included for all S1+S2+S3 calculations.

- Use local tensor values for averaged and not averaged stresses.

Table of Contents

ASME Overstressed Areas

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

ASME Overstressed Areas                                $X

*** NO OVERSTRESSED NODES IN THIS MODEL ***

Table of Contents

Highest Primary Stress Ratios

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Highest Primary Stress Ratios                          $X

Pad/Header at Junction

Pl            SPL     Primary Membrane Load Case 2

86            236     Min Prin. Stress = -39. (83% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

36%

Branch at Junction

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

218            458     Min Prin. Stress = -148. (81% Neg, 34% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

47%

Branch Transition

Pl            SPL     Primary Membrane Load Case 2

38            217     Min Prin. Stress = -35. (87% Neg, 65% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

17%

Pad Outer Edge Weld

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

230            498     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

46%

Header Outside Pad Area

Pl            SPL     Primary Membrane Load Case 2

85            236     Min Prin. Stress = -4. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

36%

Table of Contents

Highest Secondary Stress Ratios

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Highest Secondary Stress Ratios                        $X

In combination case  4 the max range stress divided

by the max component stress is 1.99. The case tensor components

are in some directions additive and so the combination

case will have HIGHER stresses than the largest of any

of the individual cases by more than 50%.

Load      Combined/Max       Combined/Max

Case        (Inside)           (Outside)

------    -------------      -------------

4         1.990               1.984

Pad/Header at Junction

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

164            498     Min Prin. Stress = -43. (73% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

32%

Branch at Junction

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

249            458     Min Prin. Stress = -170. (82% Neg, 43% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

54%

Branch Transition

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

46            458     Min Prin. Stress = -39. (84% Neg, 64% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

10%

Pad Outer Edge Weld

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

230            498     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

46%

Header Outside Pad Area

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

105            498     Min Prin. Stress = -3. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

21%

Table of Contents

Highest Fatigue Stress Ratios

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Highest Fatigue Stress Ratios                          $X

Pad/Header at Junction

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

221     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.009 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 208,642.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 801,548.

WRC 474 99% Probability Cycles = 186,207.

0%                    WRC 474 95% Probability Cycles = 258,525.

BS5500 Allowed Cycles(Curve F) = 156,950.

Membrane-to-Bending Ratio = 0.764

Bending-to-PL+PB+Q Ratio = 0.567

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Branch at Junction

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

336     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.014 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 39,497.

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 417,204.

WRC 474 99% Probability Cycles = 96,920.

1%                    WRC 474 95% Probability Cycles = 134,562.

BS5500 Allowed Cycles(Curve F) = 44,759.

Membrane-to-Bending Ratio = 0.282

Bending-to-PL+PB+Q Ratio = 0.780

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch Transition

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

46     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 68,015,488.

WRC 474 99% Probability Cycles = 15,800,615.

0%                    WRC 474 95% Probability Cycles = 21,937,166.

BS5500 Allowed Cycles(Curve F) = 7,122,108.

Membrane-to-Bending Ratio = 7.575

Bending-to-PL+PB+Q Ratio = 0.117

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pad Outer Edge Weld

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

280     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.011 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 85,213.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 707,346.

WRC 474 99% Probability Cycles = 164,323.

1%                    WRC 474 95% Probability Cycles = 228,142.

BS5500 Allowed Cycles(Curve F) = 77,806.

Membrane-to-Bending Ratio = 0.579

Bending-to-PL+PB+Q Ratio = 0.634

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Header Outside Pad Area

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

105     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.004 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.3294E10

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 5,447,098.

WRC 474 99% Probability Cycles = 1,265,410.

0%                    WRC 474 95% Probability Cycles = 1,756,863.

BS5500 Allowed Cycles(Curve F) = 591,216.

Membrane-to-Bending Ratio = 2.602

Bending-to-PL+PB+Q Ratio = 0.278

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Table of Contents

Highest Stress Ratios Per Region

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Highest Stress Ratios Per Region                       $X

Pad/Header at Junction

Pl            SPL     Primary Membrane Load Case 2

86            236     Min Prin. Stress = -39. (83% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

36%

Qb            SPS     Primary Bending Load Case 2

89            498     Min Prin. Stress = -39. (83% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

17%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

159            498     Min Prin. Stress = -39. (83% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

31%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

79            498     Min Prin. Stress = -39. (83% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

15%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

108            552     Min Prin. Stress = -39. (83% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

19%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

127            498     Min Prin. Stress = -19. (63% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

25%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

43            498     Min Prin. Stress = -19. (63% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

8%

Membrane           User     Component Evaluation Load Case 3

72            498     Min Prin. Stress = -19. (63% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

14%

Bending           User     Component Evaluation Load Case 3

57            498     Min Prin. Stress = -19. (63% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

11%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

164            498     Min Prin. Stress = -43. (73% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

32%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

93            498     Min Prin. Stress = -43. (73% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

18%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

221     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.009 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 208,642.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 801,548.

WRC 474 99% Probability Cycles = 186,207.

0%                    WRC 474 95% Probability Cycles = 258,525.

BS5500 Allowed Cycles(Curve F) = 156,950.

Membrane-to-Bending Ratio = 0.764

Bending-to-PL+PB+Q Ratio = 0.567

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

125     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.005 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 3.6436E8

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 5,486,796.

WRC 474 99% Probability Cycles = 1,274,632.

0%                    WRC 474 95% Probability Cycles = 1,769,667.

BS5500 Allowed Cycles(Curve F) = 861,803.

Membrane-to-Bending Ratio = 0.437

Bending-to-PL+PB+Q Ratio = 0.696

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch at Junction

Pl            SPL     Primary Membrane Load Case 2

72            217     Min Prin. Stress = -148. (81% Neg, 34% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

33%

Qb            SPS     Primary Bending Load Case 2

194            458     Min Prin. Stress = -148. (81% Neg, 34% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

42%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

182            458     Min Prin. Stress = -148. (81% Neg, 34% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

39%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

218            458     Min Prin. Stress = -148. (81% Neg, 34% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

47%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

111            472     Min Prin. Stress = -148. (81% Neg, 34% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

23%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

93            458     Min Prin. Stress = -69. (71% Neg, 33% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

20%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

112            458     Min Prin. Stress = -69. (71% Neg, 33% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

24%

Membrane           User     Component Evaluation Load Case 3

42            458     Min Prin. Stress = -69. (71% Neg, 33% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

9%

Bending           User     Component Evaluation Load Case 3

101            458     Min Prin. Stress = -69. (71% Neg, 33% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

22%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

209            458     Min Prin. Stress = -170. (82% Neg, 43% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

45%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

249            458     Min Prin. Stress = -170. (82% Neg, 43% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

54%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

282     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.011 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 81,702.

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 820,332.

WRC 474 99% Probability Cycles = 190,570.

1%                    WRC 474 95% Probability Cycles = 264,583.

BS5500 Allowed Cycles(Curve F) = 75,851.

Membrane-to-Bending Ratio = 0.282

Bending-to-PL+PB+Q Ratio = 0.780

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

336     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.014 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 39,497.

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 417,204.

WRC 474 99% Probability Cycles = 96,920.

1%                    WRC 474 95% Probability Cycles = 134,562.

BS5500 Allowed Cycles(Curve F) = 44,759.

Membrane-to-Bending Ratio = 0.282

Bending-to-PL+PB+Q Ratio = 0.780

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Branch Transition

Pl            SPL     Primary Membrane Load Case 2

38            217     Min Prin. Stress = -35. (87% Neg, 65% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

17%

Qb            SPS     Primary Bending Load Case 2

15            458     Min Prin. Stress = -35. (87% Neg, 65% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

3%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

39            458     Min Prin. Stress = -35. (87% Neg, 65% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

8%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

39            458     Min Prin. Stress = -35. (87% Neg, 65% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

8%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

51            472     Min Prin. Stress = -35. (87% Neg, 65% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

10%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

24            458     Min Prin. Stress = -14. (83% Neg, 60% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

5%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

23            458     Min Prin. Stress = -14. (83% Neg, 60% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

5%

Membrane           User     Component Evaluation Load Case 3

20            458     Min Prin. Stress = -14. (83% Neg, 60% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

4%

Bending           User     Component Evaluation Load Case 3

16            458     Min Prin. Stress = -14. (83% Neg, 60% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

3%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

46            458     Min Prin. Stress = -39. (84% Neg, 64% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

10%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

40            458     Min Prin. Stress = -39. (84% Neg, 64% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

8%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

46     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 68,015,488.

WRC 474 99% Probability Cycles = 15,800,615.

0%                    WRC 474 95% Probability Cycles = 21,937,166.

BS5500 Allowed Cycles(Curve F) = 7,122,108.

Membrane-to-Bending Ratio = 7.575

Bending-to-PL+PB+Q Ratio = 0.117

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

40     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.002 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.0000E11

Allowable                    "B31" Fatigue Stress Allowable = 589.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 1.0071E8

WRC 474 99% Probability Cycles = 23,396,360.

0%                    WRC 474 95% Probability Cycles = 32,482,900.

BS5500 Allowed Cycles(Curve F) = 10,840,045.

Membrane-to-Bending Ratio = 14.690

Bending-to-PL+PB+Q Ratio = 0.064

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Pad Outer Edge Weld

Pl            SPL     Primary Membrane Load Case 2

97            236     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

41%

Qb            SPS     Primary Bending Load Case 2

152            498     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

30%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

116            498     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

23%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

230            498     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

46%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

154            552     Min Prin. Stress = -2. ( 2% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

27%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

95            498     Min Prin. Stress = -1. ( 0% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

19%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

139            498     Min Prin. Stress = -1. ( 0% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

27%

Membrane           User     Component Evaluation Load Case 3

81            498     Min Prin. Stress = -1. ( 0% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

16%

Bending           User     Component Evaluation Load Case 3

73            498     Min Prin. Stress = -1. ( 0% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

14%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

126            498     Min Prin. Stress = -3. ( 3% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

25%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

207            498     Min Prin. Stress = -3. ( 3% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

41%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

170     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.007 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 932,696.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 3,152,230.

WRC 474 99% Probability Cycles = 732,292.

0%                    WRC 474 95% Probability Cycles = 1,016,695.

BS5500 Allowed Cycles(Curve F) = 343,030.

Membrane-to-Bending Ratio = 1.502

Bending-to-PL+PB+Q Ratio = 0.400

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

280     0.000 Life     Stress Concentration Factor = 1.350

MPa     0.011 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 85,213.

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 707,346.

WRC 474 99% Probability Cycles = 164,323.

1%                    WRC 474 95% Probability Cycles = 228,142.

BS5500 Allowed Cycles(Curve F) = 77,806.

Membrane-to-Bending Ratio = 0.579

Bending-to-PL+PB+Q Ratio = 0.634

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Header Outside Pad Area

Pl            SPL     Primary Membrane Load Case 2

85            236     Min Prin. Stress = -4. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

1) Pl < SPL (SUS,Membrane) Case 2

36%

Qb            SPS     Primary Bending Load Case 2

26            498     Min Prin. Stress = -4. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

2) Qb < SPS (SUS,Bending) Case 2

5%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 2

101            498     Min Prin. Stress = -4. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

3) Pl+Pb+Q < SPS (SUS,Inside) Case 2

20%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 2

101            498     Min Prin. Stress = -4. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

4) Pl+Pb+Q < SPS (SUS,Outside) Case 2

20%

S1+S2+S3             4S     Part 5 (5.3.2) Load Case 2

147            552     Min Prin. Stress = -4. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

5) S1+S2+S3 < 4S (SUS,S1+S2+S3) Case 2

26%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 3

88            498     Min Prin. Stress = -2. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

6) Pl+Pb+Q < SPS (OPE,Inside) Case 3

17%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 3

96            498     Min Prin. Stress = -2. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

7) Pl+Pb+Q < SPS (OPE,Outside) Case 3

19%

Membrane           User     Component Evaluation Load Case 3

84            498     Min Prin. Stress = -2. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

8) Membrane < User (OPE,Membrane) Case 3

16%

Bending           User     Component Evaluation Load Case 3

21            498     Min Prin. Stress = -2. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

9) Bending < User (OPE,Bending) Case 3

4%

Pl+Pb+Q            SPS     Primary+Secondary (Inner) Load Case 4

100            498     Min Prin. Stress = -3. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

15) Pl+Pb+Q < SPS (EXP,Inside) Case 4

20%

Pl+Pb+Q            SPS     Primary+Secondary (Outer) Load Case 4

105            498     Min Prin. Stress = -3. (12% Neg, 0% NegHi)

MPa            MPa     Plot Reference:

16) Pl+Pb+Q < SPS (EXP,Outside) Case 4

21%

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Inner) Load Case 4

100     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.004 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 3.3914E10

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 6,334,007.

WRC 474 99% Probability Cycles = 1,471,447.

0%                    WRC 474 95% Probability Cycles = 2,042,919.

BS5500 Allowed Cycles(Curve F) = 685,236.

Membrane-to-Bending Ratio = 2.979

Bending-to-PL+PB+Q Ratio = 0.251

Plot Reference:

17) Pl+Pb+Q+F < 2Sa (EXP,Inside) Case 4

Pl+Pb+Q+F    Damage Ratio    Primary+Secondary+Peak (Outer) Load Case 4

105     0.000 Life     Stress Concentration Factor = 1.000

MPa     0.004 Stress   Strain Concentration Factor = 1.000

Cycles Allowed for this Stress = 1.3294E10

Allowable                    "B31" Fatigue Stress Allowable = 689.5

24,846.2                    Markl Fatigue Stress Allowable = 3378.5

MPa                    WRC 474 Mean Cycles to Failure = 5,447,098.

WRC 474 99% Probability Cycles = 1,265,410.

0%                    WRC 474 95% Probability Cycles = 1,756,863.

BS5500 Allowed Cycles(Curve F) = 591,216.

Membrane-to-Bending Ratio = 2.602

Bending-to-PL+PB+Q Ratio = 0.278

Plot Reference:

18) Pl+Pb+Q+F < 2Sa (EXP,Outside) Case 4

Table of Contents

Stress Intensification Factors

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Stress Intensification Factors                         $X

Branch/Nozzle Sif Summary

Peak      Primary    Secondary      SSI

Axial   :        6.669       4.940       9.881       1.673

Inplane :        2.417       1.790       3.580       1.451

Outplane:        3.383       2.506       5.013       1.432

Torsion :        0.639       0.860       0.947       0.865

Pressure:        1.075       0.962       1.593       1.100

The above stress intensification factors are to be used

in a beam-type analysis of the piping system.  Inplane,

Outplane and Torsional sif's should be used with the

matching branch pipe whose diameter and thickness is given

below.  The axial sif should be used to intensify the

axial stress in the branch pipe calculated by F/A.  The

pressure sif should be used to intensify the nominal

pressure stress in the PARENT or HEADER, calculated

from PDo/2T. B31 calculations use mean diameters and

Section VIII calculations use outside diameters. SSIs are

based on peak stress factors and correlated test results.

Pipe OD :      114.300  mm.

Pipe Thk:        9.735  mm.

Z approx:    83595.648  cu.mm.

Z exact :    77138.852  cu.mm.

(SSI = SIF^x)        Axial   Inpl    Outpl   Tors    Pres

SIF/SSI Exponents:     0.842   0.660   0.754   0.338  -0.536

SIF/SSI exponent based on relationship between primary and

peak stress factors from the finite element analysis.

B31.3 Branch Pressure i-factor =       15.841

Header Pressure i-factor =        2.178

The B31.3 pressure i-factors should be used with with

F/A, where F is the axial force due to pressure, and

A is the area of the pipe wall. This is equivalent to

finding the pressure stress from (ip)(PD/4T).

B31.3   (Branch)

Peak Stress Sif ....    0.000         Axial

3.858         Inplane

4.783         Outplane

1.000         Torsional

B31.1  (Branch)

Peak Stress Sif ....    0.000         Axial

4.783         Inplane

4.783         Outplane

4.783         Torsional

WRC 330  (Branch)

Peak Stress Sif ....    0.000         Axial

4.422         Inplane

4.783         Outplane

4.422         Torsional

Table of Contents

Allowable Loads

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Allowable Loads                                        $X

SECONDARY                     Maximum     Conservative         Realistic

Load Type (Range):         Individual     Simultaneous        Simultaneous

Occuring       Occuring            Occuring

Axial Force      ( N     )     148391.        37417.              56125.

Inplane   Moment (mm.  N )    9879366.      1761457.            3736615.

Outplane  Moment (mm.  N )    7055976.      1258056.            2668741.

Torsional Moment (mm.  N )   37356572.      9419439.           14129159.

Pressure         (MPa    )       7.90          2.20                2.20

PRIMARY                       Maximum     Conservative         Realistic

Load Type:                 Individual     Simultaneous        Simultaneous

Occuring       Occuring            Occuring

Axial Force      ( N     )     140592.        34817.              52225.

Inplane   Moment (mm.  N )    9360079.      1639060.            3476972.

Outplane  Moment (mm.  N )    6685095.      1170639.            2483300.

Torsional Moment (mm.  N )   19489534.      4828047.            7242070.

Pressure         (MPa    )       6.20          2.20                2.20

NOTES:

1) Maximum Individual Occuring Loads are the maximum

allowed values of the respective loads if all other

load components are zero, i.e. the listed axial force

may be applied if the inplane, outplane and torsional

moments, and the pressure are zero.

2) The Conservative Allowable Simultaneous loads are

the maximum loads that can be applied simultaneously.

A conservative stress combination equation is used

that typically produces stresses within 50-70% of the

allowable stress.

3) The Realistic Allowable Simultaneous loads are the

maximum loads that can be applied simultaneously.  A

more realistic stress combination equation is used

based on experience at Paulin Research.  Stresses are

typically produced within 80-105% of the allowable.

4) Secondary allowable loads are limits for expansion

and operating piping loads.

5) Primary allowable loads are limits for weight,

primary and sustained type piping loads.

6) High D/T low pressure systems may be subject to

instability and should be checked when compressive

stresses are present.

Table of Contents

Compressive Stress Summary

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Compressive Stress Summary (MPa)                       $X

Nomenclature:

-------------

Min Stress       - Compressive Membrane and Bending Stress

Pts in Region    - No. of nodes in the model region

>5% Compression  - 5% or more of Compressive Stress Limit

>50% Compression - 50% or more of Compressive Stress Limit

Compressive Stress Limit = -0.55 Min(Sy, kEt/R), Section

slenderness ratio (elastic buckling) not considered.

>5%    >50%

Min        Pts      Compression

#  Load Type  Case    Stress    in Region   and Bending    Region

--  ---------  ----    ------   ----------  ------------  ----------------

1  SUSTAINED    2        -39.      1344      83%     0%  Pad/Header at Junction

2  OPERATING    3        -19.      1344      63%     0%  Pad/Header at Junction

3  EXPANSION    4        -43.      1344      73%     0%  Pad/Header at Junction

4  SUSTAINED    2         -2.       456       2%     0%  Pad Outer Edge Weld

5  OPERATING    3         -1.       456       0%     0%  Pad Outer Edge Weld

6  EXPANSION    4         -3.       456       3%     0%  Pad Outer Edge Weld

7  SUSTAINED    2         -4.       312      12%     0%  Header Outside Pad Area

8  OPERATING    3         -2.       312      12%     0%  Header Outside Pad Area

9  EXPANSION    4         -3.       312      12%     0%  Header Outside Pad Area

10  SUSTAINED    2       -148.      1080      81%    34%  Branch at Junction

11  OPERATING    3        -69.      1080      71%    33%  Branch at Junction

12  EXPANSION    4       -170.      1080      82%    43%  Branch at Junction

13  SUSTAINED    2        -35.       648      87%    65%  Branch Transition

14  OPERATING    3        -14.       648      83%    60%  Branch Transition

15  EXPANSION    4        -39.       648      84%    64%  Branch Transition

Table of Contents

Flexibilities

FEPipe Version 15.0           Jobname: NOZZLE                 $P

Released Jan. 2021             11:34am  APR 17,2024

Flexibilities                                          $X

The following stiffnesses should be used in a piping,

"beam-type" analysis of the intersection.  The stiff-

nesses should be inserted at the surface of the

branch/header or nozzle/vessel junction.  The general

characteristics used for the branch pipe should be:

Outside Diameter =  114.300  mm.

Wall Thickness   =    9.735  mm.

Axial Translational Stiffness   =        190063.   N /mm.

Inplane Rotational Stiffness    =      35510780.  mm. N /deg

Outplane Rotational Stiffness   =      15159243.  mm. N /deg

Torsional Rotational Stiffness  =     663682560.  mm. N /deg

Estimated Radial Shell Displacement due to Allowable Loads

SECONDARY:

Axial (mm.) =  0.781  In-Plane (mm.) =  0.254  Out-Plane (mm.) =  0.425

PRIMARY

Axial (mm.) =  0.740  In-Plane (mm.) =  0.241  Out-Plane (mm.) =  0.402

Secondary Conservative Displacement =  0.318 mm.

Secondary Realistic    Displacement =  0.552 mm.

Primary Conservative Displacement =  0.296 mm.

Primary Realistic Displacement    =  0.514 mm.

Intersection Flexibility Factors for Branch/Nozzle                                                                   :

Find axial stiffness: K = 3EI/(kd)^3   N /mm.

Find bending and torsional stiffnesses: K = EI/(kd)  mm. N per radian.

The EI product is   0.89492E+12    N mm.^2

The value of (d) to use is: 104.565  mm..

The resulting bending stiffness is in units of force x length per radian.

Axial Flexibility Factor     (k) =     2.312

Inplane Flexibility Factor   (k) =     4.206

Outplane Flexibility Factor  (k) =     9.854

Torsional Flexibility Factor (k) =     0.225

Table of Contents