## Cover
Soroush Mahestan Asaloyeh Company HDPE Project
P.o. No.: KP-40-000-PS-MA-PO-0019
Document Title: CAUSE AND EFFECT DIAGRAM
Rev.: 02
|  |  | Document No.: VP-40-000-MA-0019-0114 |  |  |  |  | Page: 1 of 4
CAUSE AND EFFECT DIAGRAM
|  |  |  | Code1 | Approved
No comment and the document is released for Manufacturing.
|  |  |  | Code2 | Approved with Minor Comments
VENDOR shall correct, revise and resubmit the document. The document can be released for Manufacturing if changes incorporated.
|  |  |  | Code3 | Commented
VENDOR shall correct, revise and resubmit the document by the date specified. The document shall be revised under the Status of “R: Revised Issue”. All corrected documents shall be resubmitted before starting the Manufacturing Process.
|  |  |  | Code4 | Not Accepted (Rejected)
VENDOR shall re-work/re-design/re-specify the contents of the documents according to the comments/ reasons for rejection. All corrected documents shall be resubmitted before starting the Manufacturing Process. In this case, VENDOR shall not proceed with subsequent work until receiving Code 1 or Code 2 or No Code from CONTRACTOR/OWNER. VENDOR shall re-submit the documents with the same revision within (10) ten working days (including transmission/mailing time) after receiving the commented documents from CONTRACTOR/OWNER.
|  |  |  | No Code | NO Code (Only for “FOR INFORMATION” Documents and “As Built DWGs”)
Document has been submitted for CONTRACTOR's Information (FI). Consistency, completeness and correctness of document content is Vendor's responsibility.
Above checking results by EIED shall in no way relieve Vendor of any liability, obligation and responsibility out of the purchase order and the mutual agreement in writing.
Date:
Dept:
Signature:
Only for internal review
|  |  |  | CV | PC | PI | EL | IN | ME | MA
|  |  |  | ST | DC | AR | PR | SA | HV | TL
02 | 13.12.2022 | R | FOR APPROVAL | H.K. | M.OS |  | A.MA |  | A.MA
01 | 20.09.2022 | R | FOR APPROVAL | H.K. | M.OS |  | A.MA |  | A.MA
00 | 13.AUG.2022 | F | FOR APPROVAL | H.K. | M.OS |  | A.MA |  | A.MA
Rev. | Date | Status | POI | PRE’D | CHK’D |  | APR’D |  | AUZ’D

## Revisions
Soroush Mahestan Asaloyeh Company HDPE Project
P.o. No.: KP-40-000-PS-MA-PO-0019
Document Title: CAUSE AND EFFECT DIAGRAM
Rev.: 02
|  |  | Document No.: VP-40-000-MA-0019-0114 | [7 empty] | Page: 2 of 4
Revision Index
Rev | 00 | 01 | 02 | 03 | 04 | 05 | Rev | 00 | 01 | 02 | 03 | 04 | 05
Sheet | [6 empty] | Sheet
1 | X | X | X
2 | X | X | X
3 | X | X | X
4 | X | X
5
6
7
8

## CAUSE AND EFFECT CHART
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Cause and Effect Diagram
|  |  |  | Document No.: EI027-HSE-VD-PR-CE-001-01 | [16 empty] | Rev.: 02 |  |  | Page: 1 of 2
[9 empty] | EFFECT | Rev.
[10 empty] | NOTES |  |  | 5 |  |  |  | 7
[10 empty] | CUSTOMER P&ID No. EI027-HSE-VD-PR-PID-002 (SHEET No.) | 7 | 7 | 7 | 7 | 7 | 6 | 2 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 5
[10 empty] | ACTION | Immediate stop of compressor | Immediate stop of oil pump RU0001A-P-01 | Immediate stop of separator oil heater | Sequential stop of compressor | Sequential stop of oil pump | Initializing to stand-by position | Initializing to stand-by position | Initializing to stand-by position | Unloading slide valve before stop oil pumps | Forbid load command of compressor capacity control | Forced unloading compressor capacity control | Alarm indication on LCP (common) and HMI (indivisual) | Trip indication on LCP (common) and HMI (indivisual) | Status indication on HMI (indivisual) | Immediate stop of condenser fan A | Immediate stop of condenser fan B
[10 empty] | DESCRIPTION | Compressor shutdown trip | Oil pump RU0001A-P-01 shutdown trip | Separator oil heater stop | Controlled stop compressor | Controlled stop oil pumps | Stop controlling Control valves | Close compresor capacity control SOV | Closing solenoid valves Refrigeration package | Return to home position command | Hold limitter of compressor capacity control | Unload limitter of compressor capacity control | Alarm indication | Trip signal to plant (Package shut down /Trip) | Status indication | Aircooler fan A shutdown tip | Aircooler fan B shutdown tip
[10 empty] | EQUIPMENT TAG No. | RU0001A-M-01 | RU0001A-P-01 | RU0001A-H-01 | RU0001A-M-01 | RU0001A-P-01 | LCV-RU0001A-01 | SOV-RU0001A-01A/B/C/D | SOV-RU0001A-02/SOV-RU0001A-03 | RU0001A-C-01 | RU0001A-C-01 | RU0001A-C-01 | XA-RU0001A-01 | XA-RU0001A-02 | Tag Nr N/A | RU0001A-M-02 | RU0001A-M-03
CAUSE
NOTES | CUSTOMER P&ID No. EI027-HSE-VD-PR-PID-002 (SHEET No.) | INSTRUMENT | DESCRIPTION |  | CLASSIFICATION | CONDITION OF ACTIVATION | PLACE OF GENERATION SOURCE | TAG No. | [19 empty] | Rev.
9 | 7 | HSS-RU0001A-01 | Emergency stop (local panel RU0001A-LCP-01) |  | Unit trip | 1 | LCP | HSSHH-RU0001A-01 |  | 1 | X | X | X |  |  | X | X | X |  |  |  |  | X |  | X | X | 1
9 | 7 | ESD-RU0001A-01 | ESD emergency shutdown |  | Unit trip | 1 | UCP | ESDHH-RU0001A-01 |  | 2 | X | X | X |  |  | X | X | X |  |  |  |  | X |  | X | X | 2
|  |  | ESD emergency shutdown CLIENT |  | Unit trip | 1 | UCP | ESDHH-RU0001A-02 |  | 3 | X | X | X |  |  | X | X | X |  |  |  |  | X |  | X | X | 3
| 2 | PIT-RU0001A-01 | Compressor Suction pressure low low |  | Unit trip | 1,3 | UCP | PISALL--RU0001A-01 |  | 4 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 4
| 2 | PIT-RU0001A-01 | Compressor Suction pressure high high |  | Unit trip | 1,3 | UCP | PISAHH--RU0001A-01 |  | 5 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 5
| 3 | PIT-RU0001A-03 | Compressor Discharge pressure high high |  | Unit trip | 1 | UCP | PISAHH--RU0001A-03 |  | 6 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 6
| 2 | PDI-RU0001A-01 | Compressor Oil supply header diff. press. low low |  | Unit trip | 1,3,4 | UCP | PDISALL-RU0001A-01 |  | 7 | X | X |  |  |  | X | X | X |  |  |  |  | X |  |  |  | 7
| 2 | TIT-RU0001A-02 | Oil header temperature High High |  | Unit trip | 1 | UCP | TISAHH-RU0001A-02 |  | 8 | X |  |  |  |  | X | X | X |  |  |  |  | X |  |  |  | 8
| 4 | PDI-RU0001A-03 | Oil Filter differential pressure high high |  | Unit trip | 1 | UCP | PDISAHH-RU0001A-03 |  | 9 | X |  |  |  | X | X | X | X |  |  |  |  | X |  |  |  | 9
10 | 3 | TIT-RU0001A-03 | Compressor Discharge temperature high high |  | Unit trip | 1 | UCP | TISAHH-RU0001A-03 |  | 10 | X |  |  |  | X | X | X | X | X |  |  |  | X |  |  |  | 10
| 2 | XL-RU0001A-01 | Compressor motor operation failure |  | Unit trip | 1,7 | MCC | XLHH-RU0001A-01 |  | 11 | X |  |  |  | X | X | X | X | X |  |  |  | X |  |  |  | 11
3.6 | 2 | II-RU0001A-01 | Compressor motor high High Amperage |  | Unit trip | 1 | MCC | IISAHH-RU0001A-01 |  | 12 | X |  |  |  | X | X | X | X | X | [7 empty] | 12
1,3,9 | 2 | XF-RU0001A-01 | Compressor motor fault |  | Unit trip | 10 | MCC | XFHH-RU0001A-01 |  | 13 | X |  |  |  | X | X | X | X | X |  |  |  | X |  |  |  | 13
3.6 | 2 | PTC-RU0001A-13 | Compressor main motor winding U temp. high high |  | Unit trip | 1 | MCC | TISAHH-RU0001A-13 |  | 16 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 16
3.6 | 2 | PTC-RU0001A-14 | Compressor main motor winding V temp. high high |  | Unit trip | 1 | MCC | TISAHH-RU0001A-14 |  | 17 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 17
3.6 | 2 | PTC-RU0001A-15 | Compressor main motor winding W temp. high high |  | Unit trip | 1 | MCC | TISAHH-RU0001A-15 |  | 18 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 18
| 6 | LIT-RU0001A-01 | Chiller Liquid level high high |  | Unit trip | 1 | UCP | LISAHH--RU0001A-01 |  | 19 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 19
| 6 | LIT-RU0001A-01 | Chiller Liquid level low low |  | Unit trip | 1,2 | UCP | LISALL--RU0001A-01 |  | 20 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 20
| 2 | PIT-RU0001A-01 | Compressor Suction pressure high |  | Unit Alarm | 1,6 | UCP | PISAH-RU0001A-01 |  | 22 | [11 empty] | X |  |  |  |  | 22
| 2 | PIT-RU0001A-01 | Compressor Suction pressure low |  | Unit Alarm | 1,6 | UCP | PISAL-RU0001A-01 |  | 23 | [11 empty] | X |  |  |  |  | 23
| 3 | PIT-RU0001A-03 | Discharge pressure high |  | Unit Alarm | 1 | UCP | PISAH-RU0001A-03 |  | 24 | [11 empty] | X |  |  |  |  | 24
| 3 | PIT-RU0001A-03 | Discharge pressure low |  | Unit Alarm |  | UCP | PISAH-RU0001A-03 |  | 25 | [11 empty] | X |  |  |  |  | 25
| 2 | PDI-RU0001A-01 | Compressor Oil supply header diff. press. low |  | Unit Alarm | 1,4 | UCP | PDISAL-RU0001A-01 |  | 26 |  |  |  |  | X | [6 empty] | X |  |  |  |  | 26
| 2 | PDI-RU0001A-01 | Compressor Oil supply header diff. press. High |  | Unit Alarm | 1,4 | UCP | PDISAH-RU0001A-01 |  | 27 |  |  |  |  | X | [6 empty] | X |  |  |  |  | 27
| 3 | PDI-RU0001A-02 | Oil separator section differential pressure high |  | Unit Alarm | 1 | UCP | PDISAH-RU0001A-02 |  | 28 | [11 empty] | X |  |  |  |  | 28
| 4 | PDI-RU0001A-03 | Oil Filter differential pressure high |  | Unit Alarm | 1 | UCP | PDISAH-RU0001A-03 |  | 29 | [11 empty] | X |  |  |  |  | 29
| 3 | TIT-RU0001A-03 | Compressor Discharge temperature high |  | Unit Alarm | 1 | UCP | TISAH-U0001A-03 |  | 30 | [11 empty] | X |  |  |  |  | 30
| 2 | TIT-RU0001A-02 | Oil supply temperature high |  | Unit Alarm | 1 | UCP | TISAH-RU0001A-02 |  | 31 | [11 empty] | X |  |  |  |  | 31
| 2 | TIT-RU0001A-02 | Oil supply temperature low |  | Unit Alarm | 1 | UCP | TISALRU0001A-02 |  | 32 | [11 empty] | X |  |  |  |  | 32
| 3 | LS-RU0001A-01 | Oil separator level low |  | Unit Alarm | 1 | UCP | LISAL-RU0001A-01 |  | 33 |  |  | X | [8 empty] | X |  |  |  |  | 33
| 4 | XL-RU0001A-03 | Oil pump RU0001A-P-01 motor operation failure |  | Unit Alarm | 1,7 | MCC | XLH-RU0001A-03 |  | 34 |  | X | [9 empty] | X |  |  |  |  | 34
| 4 | XF-RU0001A-03 | Oil pump RU0001A-P-01 motor fault |  | Unit Alarm | 1,7 | MCC | XFH-RU0001A-03 |  | 35 | [11 empty] | X |  |  |  |  | 35
| 3 | XL-RU0001A-02 | Separator oil heater operation failure |  | Unit Alarm | 1,7 | MCC | XLH-RU0001A-02 |  | 38 | [11 empty] | X |  |  |  |  | 38
2,3,9 | 3 | XF-RU0001A-02 | Separator oil heater fault |  | Unit Alarm | 10 | MCC | XFH-RU0001A-02 |  | 39 | [11 empty] | X |  |  |  |  | 39
| 6 | LIT-RU0001A-01 | Chiller liquid level high |  | Unit Alarm | 1 | UCP | LISAH-RU0001A-01 |  | 52 | [11 empty] | X |  |  |  |  | 52
| 6 | LIT-RU0001A-01 | Chiller liquid level low |  | Unit Alarm | 1 | UCP | LISAL-RU0001A-01 |  | 53 | [11 empty] | X |  |  |  |  | 53
4.9 | 3 | TS-RU0001A-01B | Separator oil heater over temp. limit switch |  | Interlock | 1 | UCP & FIELD | TSHH-RU0001A-01B |  | 55 |  |  | X | [8 empty] | X |  |  |  |  | 55
3 | 2 | II-RU0001A-01 | Compressor High motor current hold limit |  | Interlock | 1 | MCC | II-RU0001A-01 |  | 58 | [9 empty] | X |  |  |  | X |  |  | 58
| 2 | II-RU0001A-01 | Compressor High motor current unload limit |  | Interlock | 1 | MCC | II-RU0001A-01 |  | 59 | [10 empty] | X |  |  | X |  |  | 59
| 3 | PI-RU0001A-03 | High discharge pressure hold limit |  | Interlock | 1 | UCP | PI-RU0001A-03 |  | 60 | [9 empty] | X |  |  |  | X |  |  | 60
| 3 | PI-RU0001A-03 | High discharge pressure unload limit |  | Interlock | 1 | UCP | PI-RU0001A-03 |  | 61 | [10 empty] | X |  |  | X |  |  | 61
| 2 | PI-RU0001A-01 | Low suction pressure hold limit |  | Interlock | 1 | UCP | PI-RU0001A-01 |  | 62 | [9 empty] | X |  |  |  | X |  |  | 62
| 2 | PI-RU0001A-01 | Low suction pressure unload limit |  | Interlock | 1 | UCP | PI-RU0001A-01 |  | 63 | [10 empty] | X |  |  | X |  |  | 63
| 5 | VS-RU0001A-01A | Condenser motor RU0001A-M-02 vibration high high |  | Interlock | 1 | UCP | VSHH-RU0001A-01A |  | 64 | [14 empty] | X |  | 64
| 5 | VS-RU0001A-01B | Condenser motor RU0001A-M-03 vibration high high |  | Interlock | 1 | UCP | VSHH-RU0001A-01B |  | 65 | [15 empty] | X | 65
| 5 | XL-RU0001A-04A | Condenser motor RU0001A-M-02 motor operation failure |  | Unit Alarm | 1,7 | MCC | XLH-RU0001A-04A |  | 66 | [11 empty] | X |  |  | X |  | 66
1 | 5 | XF-RU0001A-04A | Condenser motor RU0001A-M-02 motor fault |  | Unit Alarm | 10 | MCC | XFH-RU0001A-04A |  | 67 | [11 empty] | X |  |  |  | X | 67
| 5 | XL-RU0001A-04B | Condenser motor RU0001A-M-03 motor operation failure |  | Unit Alarm | 1,7 | MCC | XLH-RU0001A-04B |  | 68 | [11 empty] | X |  |  | X |  | 68
1 | 5 | XF-RU0001A-04B | Condenser motor RU0001A-M-03 motor fault |  | Unit Alarm | 10 | MCC | XFH-RU0001A-04B |  | 69 | [11 empty] | X |  |  |  | X | 69
Document Title: CAUSE AND EFFECT DIAGRAM
Rev.: 02
Page: 3 Of 3
NOTES: 1 Include any electrical faults detected by MCC. (e.g. over load, over current, low/high voltage, ground fault, open phase, reverse phase, etc.) 2 Include any electrical faults detected by MCC, and "Separator oil heater over temp. limit switch". status and "Separator oil heater box cut-out switch" status. 3 Activate by "fault signal" from MCC. Safety interlock to be created by MCC. 4 Activate "fault signal" to PLC. Alarm indication to be created commonly by "fault signal". 5 Local reset switch in the heater terminal box. 6 Cable directly connected to MCC from local equipment. 7 Caused by unit stop status and compressor stop status. 8 UCP: Unit control panel (PLC panel) / LCP: Local control panel / Local: Local equipment. MCC: Motor control centre / CCR: Central control room. 9 Source of trip must be cleared by reset , before possible reset on the HMI (UCP). 10 Only one compressor is able to operate at the same time. In case of indicated trip, stand-by compressor can be started 11 Main motor start permissive 3/2 cold/hot start-ups 12 This diagram is prepared for RU-0001A and is typical for RU-0001B with changing suffix of all tag numbers from "A" to "B". e.g. PG-RU0001B-01 | [10 empty] | Condition of activation : 1 Activate after delay timer has expired (if delay timer is applicable). 2 Activate when unit status is ”in operation”. ("In operation" = status from compressor started by start order until stop order has been received). 3 Activate when compressor motor running confirmation is activated. 4 Activate when oil pump motor running confirmation is activated. 5 Activate after 60 second from when unit status is ”in operation”. 6 Activate after 60 second from when compressor motor running confirmation is activated. 7 Activated by No running confirmation from MCC after start signal delivered, or Remaining running confirmation from MCC after stop signal delivered. 8 Activated by No running confirmation of oil pumps when compressor running. 9 Activated by both oil pump has motor fault and/or operation failure. 10 Activated by fault status signal from MCC. 11 Signal from Control room
REFRIGERATION PACKAGE
RU-0001A