## COVER
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 | [6 empty] | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [5 empty] | Page: 1
Project no. : PPJP-99ME04 | [6 empty] | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
Pressure Transmitter Data Sheet
| VENDOR: | [5 empty] | KASRAVAND |  | VENDOR'S JOB: |  |  |  | 1082
| Purchase Order: | [5 empty] | PPJPC-1400-17 |  | Item: |  |  |  | ????
| Component: | [5 empty] | ????? |  | Equipment: |  |  |  | RTO
|  | Status Code | [5 empty] | Eng. |  | Dept. |  |  | Date
Comment status code:
|  |  | AP - Approved and released for Manufacture | [6 empty] | NC - No Comments
|  |  | CO - Not Approved | [6 empty] | AC - Approved with Comments
RE - Rejected
IMPORTANT: Permission to proceed does not constitute acceptance or approval of design details, calculations, analyses, test methods or materials developed or selected by the supplier and does not relieve supplier from full compliance with contractual obligation.
01 | 2024-02-11 |  |  | IFA |  | Issued For Approval |  |  |  |  | O.S | A.M | H.O
00 | 2022-03-02 |  |  | IFA |  | Issued For Approval |  |  |  |  | O.S | A.M | H.O
Rev | Date |  |  | Class |  | Status |  |  |  |  | Prepared | Checked | Approved | Prepared | Checked | Approved
[11 empty] | NOVA SYNERGY/KASRAVAND |  |  | TCM / JSC

## INDEX
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 | [5 empty] | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [10 empty] | Page: 2
Project no. : PPJP-99ME04 | [5 empty] | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
PAGE | REVISION | [6 empty] | PAGE | REVISION | [6 empty] | PAGE |  | REVISION
| 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | x | x | [5 empty] | 79 | [7 empty] | 157
2 | x | x | [5 empty] | 80 | [7 empty] | 158
3 | x | x | [5 empty] | 81 | [7 empty] | 159
4 | x | x | [5 empty] | 82 | [7 empty] | 160
5 | x | x | [5 empty] | 83 | [7 empty] | 161
6 | x | x | [5 empty] | 84 | [7 empty] | 162
7 | x | x | [5 empty] | 85 | [7 empty] | 163
8 | x | x | [5 empty] | 86 | [7 empty] | 164
9 | x | x | [5 empty] | 87 | [7 empty] | 165
10 | x | x | [5 empty] | 88 | [7 empty] | 166
11 | x | x | [5 empty] | 89 | [7 empty] | 167
12 | x | x | [5 empty] | 90 | [7 empty] | 168
13 |  | x | [5 empty] | 91 | [7 empty] | 169
14 |  | x | [5 empty] | 92 | [7 empty] | 170
15 | [7 empty] | 93 | [7 empty] | 171
16 | [7 empty] | 94 | [7 empty] | 172
17 | [7 empty] | 95 | [7 empty] | 173
18 | [7 empty] | 96 | [7 empty] | 174
19 | [7 empty] | 97 | [7 empty] | 175
20 | [7 empty] | 98 | [7 empty] | 176
21 | [7 empty] | 99 | [7 empty] | 177
22 | [7 empty] | 100 | [7 empty] | 178
23 | [7 empty] | 101 | [7 empty] | 179
24 | [7 empty] | 102 | [7 empty] | 180
25 | [7 empty] | 103 | [7 empty] | 181
26 | [7 empty] | 104 | [7 empty] | 182
27 | [7 empty] | 105 | [7 empty] | 183
28 | [7 empty] | 106 | [7 empty] | 184
29 | [7 empty] | 107 | [7 empty] | 185
30 | [7 empty] | 108 | [7 empty] | 186
31 | [7 empty] | 109 | [7 empty] | 187
32 | [7 empty] | 110 | [7 empty] | 188
33 | [7 empty] | 111 | [7 empty] | 189
34 | [7 empty] | 112 | [7 empty] | 190
35 | [7 empty] | 113 | [7 empty] | 191
36 | [7 empty] | 114 | [7 empty] | 192
37 | [7 empty] | 115 | [7 empty] | 193
38 | [7 empty] | 116 | [7 empty] | 194
39 | [7 empty] | 117 | [7 empty] | 195
40 | [7 empty] | 118 | [7 empty] | 196
41 | [7 empty] | 119 | [7 empty] | 197
42 | [7 empty] | 120 | [7 empty] | 198
43 | [7 empty] | 121 | [7 empty] | 199
44 | [7 empty] | 122 | [7 empty] | 200
45 | [7 empty] | 123 | [7 empty] | 201
46 | [7 empty] | 124 | [7 empty] | 202
47 | [7 empty] | 125 | [7 empty] | 203
48 | [7 empty] | 126 | [7 empty] | 204
49 | [7 empty] | 127 | [7 empty] | 205
50 | [7 empty] | 128 | [7 empty] | 206
51 | [7 empty] | 129 | [7 empty] | 207
52 | [7 empty] | 130 | [7 empty] | 208
53 | [7 empty] | 131 | [7 empty] | 209
54 | [7 empty] | 132 | [7 empty] | 210
55 | [7 empty] | 133 | [7 empty] | 211
56 | [7 empty] | 134 | [7 empty] | 212
57 | [7 empty] | 135 | [7 empty] | 213
58 | [7 empty] | 136 | [7 empty] | 214
59 | [7 empty] | 137 | [7 empty] | 215
60 | [7 empty] | 138 | [7 empty] | 216
61 | [7 empty] | 139 | [7 empty] | 217
62 | [7 empty] | 140 | [7 empty] | 218
63 | [7 empty] | 141 | [7 empty] | 219
64 | [7 empty] | 142 | [7 empty] | 220
65 | [7 empty] | 143 | [7 empty] | 221
66 | [7 empty] | 144 | [7 empty] | 222
67 | [7 empty] | 145 | [7 empty] | 223
68 | [7 empty] | 146 | [7 empty] | 224
69 | [7 empty] | 147 | [7 empty] | 225
70 | [7 empty] | 148 | [7 empty] | 226
71 | [7 empty] | 149 | [7 empty] | 227
72 | [7 empty] | 150 | [7 empty] | Appendix
73 | [7 empty] | 151
74 | [7 empty] | 152 | [7 empty] | Att. 1
75 | [7 empty] | 153 | [7 empty] | Att. 2
76 | [7 empty] | 154 | [7 empty] | Att. 3
77 | [7 empty] | 155 | [7 empty] | Att. 4
78 | [7 empty] | 156 | [7 empty] | Att. 5

## PIT-RU0001AB-01
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [8 empty] | Page: 3
Project no. : PPJP-99ME04 |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
GENERAL
1 | Tag No. | PIT-RU0001A-01,PIT-RU0001B-01 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Compressor Suction | [5 empty] | 8
3 | Line No. | 5"-PR-RU0001(A/B)01-ML3R1-C | [5 empty] | 9
4 | Line Size | Line Schedule |  | 5" |  |  |  | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | EI027-HSE-VD-PR-PID-002 (2/7) | [5 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 10.3
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPT Female
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Gas |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 4.65 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | -0.17 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | PROPANE |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G | FV | 22 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -45 | 120 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-02
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [8 empty] | Page: 4
Project no. : PPJP-99ME04 |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
GENERAL
1 | Tag No. | PIT-RU0001A-02,PIT-RU0001B-02 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Compressor Lubricant Inlet | [5 empty] | 8
3 | Line No. | 2"-OI-RU0001A05-MS3R0-E | [5 empty] | 9
4 | Line Size | Line Schedule |  | 2" |  |  |  | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | EI027-HSE-VD-PR-PID-002 (2/7) | [5 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | Lubricant Oil |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Liquid |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 22.5 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 60 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 26 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-03
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [8 empty] | Page: 7
Project no. : PPJP-99ME04 |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
GENERAL
1 | Tag No. | PIT-RU0001A-03,PIT-RU0001B-03 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Separator | [5 empty] | 8
3 | Line No. | [6 empty] | 9
4 | Line Size | Line Schedule | [5 empty] | 10
5 | Equipment No. | [6 empty] | 11
6 | PID No. | EI027-HSE-VD-PR-PID-002 (3/7) | [5 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Gas |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 20.2 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 73.5 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-04
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [8 empty] | Page: 8
Project no. : PPJP-99ME04 |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
GENERAL
1 | Tag No. | PIT-RU0001A-04,PIT-RU0001B-04 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Separator | [5 empty] | 8
3 | Line No. | [6 empty] | 9
4 | Line Size | Line Schedule | [5 empty] | 10
5 | Equipment No. | RU0001(A/B)-D-01 | [5 empty] | 11
6 | PID No. | EI027-HSE-VD-PR-PID-002 (3/7) | [5 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments |  |  | Yes
44 | Phase Fluid |  |  | Gas |  |  |  | 85 | ASME UV STAMP Required |  |  | -
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 19.8 |  |  | 87 | Test Requirements |  |  | Yes
47 | Temperature |  | °C |  | 73.5 |  |  | 88 | Factory Configuration |  |  | 2 Valve
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | 316 SS
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | 1/2" - NPTF
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE |  |  | -
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | No
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-05
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [8 empty] | Page: 11
Project no. : PPJP-99ME04 |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
GENERAL
1 | Tag No. | PIT-RU0001A-05,PIT-RU0001B-05 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Cooler Discharge | [5 empty] | 8
3 | Line No. | 2"-0I-RU0001(A/B)02-MC3R1-E | [5 empty] | 9
4 | Line Size | Line Schedule |  | 2" |  |  |  | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | EI027-HSE-VD-PR-PID-002 (3/7) | [5 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | Oil |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Liquid |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 19.7 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 60 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-06
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Pressure Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003 | [8 empty] | Page: 12
Project no. : PPJP-99ME04 |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-003
GENERAL
1 | Tag No. | PIT-RU0001A-06,PIT-RU0001B-06 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Pump Suction | [5 empty] | 8
3 | Line No. | 2"-0I-68003A-MS3R0-E | [5 empty] | 9
4 | Line Size | Line Schedule | [5 empty] | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | PJ-80-KAS-PR-PID-4100-0001-001 (7/9) | [5 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | Oil |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Liquid |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 19.7 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 60 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE |  |  | -
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED