## COVER
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Temperature Transmitter Data Sheet
Contract No.: PPJPC-1400-17 | [6 empty] | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004 | [5 empty] | Page: 1
Project no. : PPJP-99ME04 | [6 empty] | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004
Temperature Transmitter Data Sheet
| VENDOR: | [5 empty] | KASRAVAND |  | VENDOR'S JOB: |  |  |  | 1082
| Purchase Order: | [5 empty] | PPJPC-1400-17 |  | Item: |  |  |  | ????
| Component: | [5 empty] | ????? |  | Equipment: |  |  |  | RTO
|  | Status Code | [5 empty] | Eng. |  | Dept. |  |  | Date
Comment status code:
|  |  | AP - Approved and released for Manufacture | [6 empty] | NC - No Comments
|  |  | CO - Not Approved | [6 empty] | AC - Approved with Comments
RE - Rejected
IMPORTANT: Permission to proceed does not constitute acceptance or approval of design details, calculations, analyses, test methods or materials developed or selected by the supplier and does not relieve supplier from full compliance with contractual obligation.
01 | 2024-02-11 |  |  | IFA |  | Issued For Approval |  |  |  |  | O.S | A.M | H.O
00 | 2022-03-02 |  |  | IFA |  | Issued For Approval |  |  |  |  | O.S | A.M | H.O
Rev | Date |  |  | Class |  | Status |  |  |  |  | Prepared | Checked | Approved | Prepared | Checked | Approved
[11 empty] | NOVA SYNERGY/KASRAVAND |  |  | TCM / JSC

## INDEX
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Temperature Transmitter Data Sheet
Contract No.: PPJPC-1400-17 | [5 empty] | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004 | [10 empty] | Page: 2
Project no. : PPJP-99ME04 | [5 empty] | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004
PAGE | REVISION | [6 empty] | PAGE | REVISION | [6 empty] | PAGE |  | REVISION
| 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | x | x | [5 empty] | 79 | [7 empty] | 157
2 | x | x | [5 empty] | 80 | [7 empty] | 158
3 | x | x | [5 empty] | 81 | [7 empty] | 159
4 | x | x | [5 empty] | 82 | [7 empty] | 160
5 | x | x | [5 empty] | 83 | [7 empty] | 161
6 | x | x | [5 empty] | 84 | [7 empty] | 162
7 | x | x | [5 empty] | 85 | [7 empty] | 163
8 | x | x | [5 empty] | 86 | [7 empty] | 164
9 | x | x | [5 empty] | 87 | [7 empty] | 165
10 | [7 empty] | 88 | [7 empty] | 166
11 | [7 empty] | 89 | [7 empty] | 167
12 | [7 empty] | 90 | [7 empty] | 168
13 | [7 empty] | 91 | [7 empty] | 169
14 | [7 empty] | 92 | [7 empty] | 170
15 | [7 empty] | 93 | [7 empty] | 171
16 | [7 empty] | 94 | [7 empty] | 172
17 | [7 empty] | 95 | [7 empty] | 173
18 | [7 empty] | 96 | [7 empty] | 174
19 | [7 empty] | 97 | [7 empty] | 175
20 | [7 empty] | 98 | [7 empty] | 176
21 | [7 empty] | 99 | [7 empty] | 177
22 | [7 empty] | 100 | [7 empty] | 178
23 | [7 empty] | 101 | [7 empty] | 179
24 | [7 empty] | 102 | [7 empty] | 180
25 | [7 empty] | 103 | [7 empty] | 181
26 | [7 empty] | 104 | [7 empty] | 182
27 | [7 empty] | 105 | [7 empty] | 183
28 | [7 empty] | 106 | [7 empty] | 184
29 | [7 empty] | 107 | [7 empty] | 185
30 | [7 empty] | 108 | [7 empty] | 186
31 | [7 empty] | 109 | [7 empty] | 187
32 | [7 empty] | 110 | [7 empty] | 188
33 | [7 empty] | 111 | [7 empty] | 189
34 | [7 empty] | 112 | [7 empty] | 190
35 | [7 empty] | 113 | [7 empty] | 191
36 | [7 empty] | 114 | [7 empty] | 192
37 | [7 empty] | 115 | [7 empty] | 193
38 | [7 empty] | 116 | [7 empty] | 194
39 | [7 empty] | 117 | [7 empty] | 195
40 | [7 empty] | 118 | [7 empty] | 196
41 | [7 empty] | 119 | [7 empty] | 197
42 | [7 empty] | 120 | [7 empty] | 198
43 | [7 empty] | 121 | [7 empty] | 199
44 | [7 empty] | 122 | [7 empty] | 200
45 | [7 empty] | 123 | [7 empty] | 201
46 | [7 empty] | 124 | [7 empty] | 202
47 | [7 empty] | 125 | [7 empty] | 203
48 | [7 empty] | 126 | [7 empty] | 204
49 | [7 empty] | 127 | [7 empty] | 205
50 | [7 empty] | 128 | [7 empty] | 206
51 | [7 empty] | 129 | [7 empty] | 207
52 | [7 empty] | 130 | [7 empty] | 208
53 | [7 empty] | 131 | [7 empty] | 209
54 | [7 empty] | 132 | [7 empty] | 210
55 | [7 empty] | 133 | [7 empty] | 211
56 | [7 empty] | 134 | [7 empty] | 212
57 | [7 empty] | 135 | [7 empty] | 213
58 | [7 empty] | 136 | [7 empty] | 214
59 | [7 empty] | 137 | [7 empty] | 215
60 | [7 empty] | 138 | [7 empty] | 216
61 | [7 empty] | 139 | [7 empty] | 217
62 | [7 empty] | 140 | [7 empty] | 218
63 | [7 empty] | 141 | [7 empty] | 219
64 | [7 empty] | 142 | [7 empty] | 220
65 | [7 empty] | 143 | [7 empty] | 221
66 | [7 empty] | 144 | [7 empty] | 222
67 | [7 empty] | 145 | [7 empty] | 223
68 | [7 empty] | 146 | [7 empty] | 224
69 | [7 empty] | 147 | [7 empty] | 225
70 | [7 empty] | 148 | [7 empty] | 226
71 | [7 empty] | 149 | [7 empty] | 227
72 | [7 empty] | 150 | [7 empty] | Appendix
73 | [7 empty] | 151
74 | [7 empty] | 152 | [7 empty] | Att. 1
75 | [7 empty] | 153 | [7 empty] | Att. 2
76 | [7 empty] | 154 | [7 empty] | Att. 3
77 | [7 empty] | 155 | [7 empty] | Att. 4
78 | [7 empty] | 156 | [7 empty] | Att. 5

## TIT-RU0001AB-01
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Temperature Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004 | [6 empty] | Page: 3
Project no. : PPJP-99ME04 |  |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004
GENERAL
1 | Tag No. |  | TIT-RU0001A-01,TIT-RU0001B-01 |  |  |  |  | 7 | AREA Classification |  | Zone 2 IIB T3
2 | Service |  | Compressor Suction |  |  |  |  | 8
3 | Line No. |  | 5"-PR-RU0001(A/B)01-ML3R1-C |  |  |  |  | 9
4 | Line Size |  | Line Schedule |  | 5" |  |  | 10
5 | Equipment No. |  | - |  |  |  |  | 11
6 | PID No. |  | EI027-HSE-VD-PR-PID-002 (2/7) |  |  |  |  | 12
| ELEMENT / THERMOWELL | [7 empty] | PROCESS DATA
13 | Element |  | Tolerance as per |  | RTD | IEC-60751 |  | 56 | Fluid Name / Phase |  | Propane / Vapor
14 | Element Type |  |  |  | PT100Ω-0°C-Resistance |  |  | 57 | Solids in Fluid | Kg | -
15 | Element Wires Material |  |  |  | Single RTD PT100 (3W) |  |  | 58 | Operating Conditions |  | Min | Norm |  | Max
16 | Quantity |  |  |  | 1 |  |  | 59 | Operating Pressure | bar A |  | 4.7
17 | Element External Diameter |  |  |  | 6 mm |  |  | 60 | Temperature | °C |  | -0.07
18 | Wire Size |  | Insulation |  | 0.5 mm | Mg. Oxide |  | 61 | Flow | Kg/h | 2847
19 | Sheath Material |  |  |  | 316 SS |  |  | 62 | Max. Velocity | m/s | 4.2
20 | Connection Type |  |  |  | 3 Wire |  |  | 63 | Design Pressure Min / Max | bar G | FV |  | 22
21 | Spring Load |  |  |  | Yes |  |  | 64 | Design Temp. Min / Max | ° C | -29 |  | 120
22 | Hot Junction |  |  |  | - |  |  | 65 | Corrosive Agents |  | -
23 | Thermowell Construction |  |  |  | Barstock Drilled |  |  | 66 | Toxic Agents |  | -
24 | Standard Drawing |  |  |  | - |  |  | 67 | Density | Kg/m3 |  | 10.22
25 | Thermowell Material |  |  |  | 316L SS |  |  | 68 | Viscosity | cP |  | 0.0078
26 | Insertion Length "U" |  |  |  | 80 mm |  |  | 69
27 | Lagging Extension "T" |  |  |  | 50 mm |  |  |  | TRANSMITTER
28 | Overall Thermowell Extension |  |  |  | 130 mm |  |  | 70 | Location / Mounting |  | Local / vertical
29 | Length Code |  |  |  | - |  |  | 71 | Electrical Protection |  | Ex ia IIB T3
30 | Flange Material |  |  |  | - |  |  | 72 | Housing Material |  | Die-cast AL
31 | Size | Rating |  | Facing | 1/2" BSPT |  |  | 73 | Burn-out direction |  | -
32 | Internal connection |  |  |  | M20 x 1.5 |  |  | 74 | Cold Junction Compensation
33 | Thermowell Supply |  |  |  | Yes |  |  | 75 | Electical Connections |  | Yes
34 | Thermowell Tag | [6 empty] | 76 | Cable Entries Qty. |  | 2
35 | Stamping |  |  |  | Engraved |  |  | 77 | Integral Indicator / Mounting |  | Yes
36 | Process Connection |  |  |  | Thread |  |  | 78 | IP Rating |  | IP 65
| EXTENSION NIPPLE | [6 empty] | 79 | Accuracy |  | +/- 0.2% F.S.
37 | Extension Type |  |  |  | Nipple Union |  |  | 80 | Calibration Range | °C | -50 |  | - | 150
38 | Nipple Length |  |  |  | 50 mm |  |  | 81 | Instrument Range | °C | -50 |  | - | 150
39 | Process Connection |  |  |  | 1/2" |  |  | 82 | Cable Gland size |  | M20 x 1.5
40 | Compression Gland Material |  |  |  | Stainless Steel |  |  |  | COMMUNICATION
| HEAD | [6 empty] | 83 | Power Supply / From |  | 24 Vdc |  | System
41 | Head Type |  |  |  | Standard |  |  | 84 | Output Signal |  | 4-20 mA Hart
42 | Head Material |  |  |  | Stainless Steel |  |  | 85
43 | Electical enclosure Class |  |  |  | IP 65 |  |  |  | CONFIGURATION
44 | Electrical Connections |  |  |  | M20 x 1.5 |  |  | 86 | Input Range Limits | °C | -50 | °C | - | 150
45 | Terminal Block |  |  |  | Lead Wires |  |  | 87 | Factory Configuration |  | Yes
46 | Screw Cover / Chain |  |  |  | No |  |  | 88 | Factory Calibration |  | Yes
47 | Specific Span |  |  |  | -50 | - | 150 | 89
48 | [8 empty] | REQUIREMENTS AND TEST
49 | [7 empty] | 90 | NACE Requirments |  | No
| ACCESSORIES | [6 empty] | 91 | Hydro Test |  | Yes
50 | Sunshade |  |  |  | No |  |  | 92 | Material Certification |  | 3.1 Material Certificate
51 | Nipple |  |  |  | No |  |  | 93 | Test Requirements |  | Yes
52 | Chain |  |  |  | No |  |  | 94 | Factory Checking |  | Yes
53 | [7 empty] | 95 | Factory Calibration |  | N/A
54 | [7 empty] | 96 | PMI |  | No
55 | [7 empty] | 97 | NDE |  | Manufacturer's Standard
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  |  | WIKA |  |  | 104 | Note 1: Element and transmitter installed on same housing. Transmitter to be locally mounted attached on temperature element Note 2: Wake frequency calculation will be submitted by Vendor.
99 | Model Number |  |  |  | TIF50/TW10
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## TIT-RU0001AB-02
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Temperature Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004 | [6 empty] | Page: 4
Project no. : PPJP-99ME04 |  |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004
GENERAL
1 | Tag No. |  | TIT-RU0001A-02,TIT-RU0001B-02 |  |  |  |  | 7 | AREA Classification |  | Zone 2 IIB T3
2 | Service |  | Lub Oil |  |  |  |  | 8
3 | Line No. |  | 2"-0I-RU0001(A/B)5-MS3R0-E |  |  |  |  | 9
4 | Line Size |  | Line Schedule |  | 2" |  |  | 10
5 | Equipment No. |  | - |  |  |  |  | 11
6 | PID No. |  | EI027-HSE-VD-PR-PID-002 (2/7) |  |  |  |  | 12
| ELEMENT / THERMOWELL | [7 empty] | PROCESS DATA
13 | Element |  | Tolerance as per |  | RTD | IEC-60751 |  | 56 | Fluid Name / Phase |  | Lubricant Oil / Liquid
14 | Element Type |  |  |  | PT100Ω-0°C-Resistance |  |  | 57 | Solids in Fluid | Kg | -
15 | Element Wires Material |  |  |  | Single RTD PT100 (3W) |  |  | 58 | Operating Conditions |  | Min | Norm |  | Max
16 | Quantity |  |  |  | 1 |  |  | 59 | Operating Pressure | bar A |  | 22.5
17 | Element External Diameter |  |  |  | 6 mm |  |  | 60 | Temperature | °C |  | 60
18 | Wire Size |  | Insulation |  | 0.5 mm | Mg. Oxide |  | 61 | Flow | Kg/h | 3208
19 | Sheath Material |  |  |  | 316 SS |  |  | 62 | Max. Velocity | m/s | 0.5
20 | Connection Type |  |  |  | 3 Wire |  |  | 63 | Design Pressure Min / Max | bar G |  |  | 26
21 | Spring Load |  |  |  | Yes |  |  | 64 | Design Temp. Min / Max | ° C | -29 |  | 100
22 | Hot Junction |  |  |  | - |  |  | 65 | Corrosive Agents |  | -
23 | Thermowell Construction |  |  |  | Barstock Drilled |  |  | 66 | Toxic Agents |  | -
24 | Standard Drawing |  |  |  | - |  |  | 67 | Density | Kg/m3 |  | 1005
25 | Thermowell Material |  |  |  | 316L SS |  |  | 68 | Viscosity | cP |  | 12
26 | Insertion Length "U" |  |  |  | 50 mm |  |  | 69
27 | Lagging Extension "T" |  |  |  | 50 mm |  |  |  | TRANSMITTER
28 | Overall Thermowell Extension |  |  |  | 100 mm |  |  | 70 | Location / Mounting |  | Local / vertical
29 | Length Code |  |  |  | - |  |  | 71 | Electrical Protection |  | Ex ia IIB T3
30 | Flange Material |  |  |  | - |  |  | 72 | Housing Material |  | Die-cast AL
31 | Size | Rating |  | Facing | 1/2" BSPT |  |  | 73 | Burn-out direction |  | -
32 | Internal connection |  |  |  | M20 x 1.5 |  |  | 74 | Cold Junction Compensation
33 | Thermowell Supply |  |  |  | Yes |  |  | 75 | Electical Connections |  | Yes
34 | Thermowell Tag | [6 empty] | 76 | Cable Entries Qty. |  | 2
35 | Stamping |  |  |  | Engraved |  |  | 77 | Integral Indicator / Mounting |  | Yes
36 | Process Connection |  |  |  | Thread |  |  | 78 | IP Rating |  | IP 65
| EXTENSION NIPPLE | [6 empty] | 79 | Accuracy |  | +/- 0.2% F.S.
37 | Extension Type |  |  |  | Nipple Union |  |  | 80 | Calibration Range | °C | -50 |  | - | 150
38 | Nipple Length |  |  |  | 50 mm |  |  | 81 | Instrument Range | °C | -50 |  | - | 150
39 | Process Connection |  |  |  | - |  |  | 82 | Cable Gland size |  | M20 x 1.5
40 | Compression Gland Material |  |  |  | Stainless Steel |  |  |  | COMMUNICATION
| HEAD | [6 empty] | 83 | Power Supply / From |  | 24 Vdc |  | System
41 | Head Type |  |  |  | Standard |  |  | 84 | Output Signal |  | 4-20 mA Hart
42 | Head Material |  |  |  | Stainless Steel |  |  | 85
43 | Electical enclosure Class |  |  |  | IP 65 |  |  |  | CONFIGURATION
44 | Electrical Connections |  |  |  | M20 x 1.5 |  |  | 86 | Input Range Limits | °C | - | °C | - | -
45 | Terminal Block |  |  |  | Lead Wires |  |  | 87 | Factory Configuration |  | Yes
46 | Screw Cover / Chain |  |  |  | No |  |  | 88 | Factory Calibration |  | Yes
47 | Specific Span |  |  |  | -50 | - | 150 | 89
48 | [8 empty] | REQUIREMENTS AND TEST
49 | [7 empty] | 90 | NACE Requirments |  | No
| ACCESSORIES | [6 empty] | 91 | Hydro Test |  | Yes
50 | Sunshade |  |  |  | No |  |  | 92 | Material Certification |  | 3.1 Material Certificate
51 | Nipple |  |  |  | No |  |  | 93 | Test Requirements |  | Yes
52 | Chain |  |  |  | No |  |  | 94 | Factory Checking |  | Yes
53 | [7 empty] | 95 | Factory Calibration |  | N/A
54 | [7 empty] | 96 | PMI |  | No
55 | [7 empty] | 97 | NDE |  | Manufacturer's Standard
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  |  | WIKA |  |  | 104 | Note 1: Element and transmitter installed on same housing. Transmitter to be locally mounted attached on temperature element Note 2: Wake frequency calculation will be submitted by Vendor.
99 | Model Number |  |  |  | TIF50/TW10
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## TIT-RU0001AB-03
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
Temperature Transmitter Data Sheet
Contract No.: PPJPC-1400-17 |  |  |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004 | [6 empty] | Page: 7
Project no. : PPJP-99ME04 |  |  |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-004
GENERAL
1 | Tag No. |  | TIT-RU0001A-03,TIT-RU0001B-03 |  |  |  |  | 7 | AREA Classification |  | Zone 2 IIB T3
2 | Service |  | Oil Separator |  |  |  |  | 8
3 | Line No. | [6 empty] | 9
4 | Line Size |  | Line Schedule |  |  |  |  | 10
5 | Equipment No. |  | RU0001(A/B)-D-01 |  |  |  |  | 11
6 | PID No. |  | EI027-HSE-VD-PR-PID-002 (3/7) |  |  |  |  | 12
| ELEMENT / THERMOWELL | [7 empty] | PROCESS DATA
13 | Element |  | Tolerance as per |  | RTD | IEC-60751 |  | 56 | Fluid Name / Phase |  | Lubricant Oil / Liquid
14 | Element Type |  |  |  | PT100Ω-0°C-Resistance |  |  | 57 | Solids in Fluid | Kg | -
15 | Element Wires Material |  |  |  | Single RTD PT100 (3W) |  |  | 58 | Operating Conditions |  | Min | Norm |  | Max
16 | Quantity |  |  |  | 1 |  |  | 59 | Operating Pressure | bar A |  | 20.2
17 | Element External Diameter |  |  |  | 6 mm |  |  | 60 | Temperature | °C |  | 73.5
18 | Wire Size |  | Insulation |  | 0.5 mm | Mg. Oxide |  | 61 | Flow | Kg/h | -
19 | Sheath Material |  |  |  | 316 SS |  |  | 62 | Max. Velocity | m/s | -
20 | Connection Type |  |  |  | 3 Wire |  |  | 63 | Design Pressure Min / Max | bar G |  |  | 22
21 | Spring Load |  |  |  | Yes |  |  | 64 | Design Temp. Min / Max | ° C | -29 |  | 100
22 | Hot Junction |  |  |  | - |  |  | 65 | Corrosive Agents |  | -
23 | Thermowell Construction |  |  |  | Barstock Drilled |  |  | 66 | Toxic Agents |  | -
24 | Standard Drawing |  |  |  | - |  |  | 67 | Density | Kg/m3 |  | 1005
25 | Thermowell Material |  |  |  | 316L SS |  |  | 68 | Viscosity | cP |  | 12
26 | Insertion Length "U" |  |  |  | 200 mm |  |  | 69
27 | Lagging Extension "T" |  |  |  | 50 mm |  |  |  | TRANSMITTER
28 | Overall Thermowell Extension |  |  |  | 250 mm |  |  | 70 | Location / Mounting |  | Local / vertical
29 | Length Code |  |  |  | - |  |  | 71 | Electrical Protection |  | Ex ia IIB T3
30 | Flange Material |  |  |  | - |  |  | 72 | Housing Material |  | Die-cast AL
31 | Size | Rating |  | Facing | 1/2" BSPT |  |  | 73 | Burn-out direction |  | -
32 | Internal connection |  |  |  | M20 x 1.5 |  |  | 74 | Cold Junction Compensation
33 | Thermowell Supply |  |  |  | Yes |  |  | 75 | Electical Connections |  | Yes
34 | Thermowell Tag | [6 empty] | 76 | Cable Entries Qty. |  | 2
35 | Stamping |  |  |  | Engraved |  |  | 77 | Integral Indicator / Mounting |  | Yes
36 | Process Connection |  |  |  | Thread |  |  | 78 | IP Rating |  | IP 65
| EXTENSION NIPPLE | [6 empty] | 79 | Accuracy |  | +/- 0.2% F.S.
37 | Extension Type |  |  |  | Nipple Union |  |  | 80 | Calibration Range | °C | -50 |  | - | 150
38 | Nipple Length |  |  |  | 100 mm |  |  | 81 | Instrument Range | °C | -50 |  | - | 150
39 | Process Connection |  |  |  | - |  |  | 82 | Cable Gland size |  | M20 x 1.5
40 | Compression Gland Material |  |  |  | Stainless Steel |  |  |  | COMMUNICATION
| HEAD | [6 empty] | 83 | Power Supply / From |  | 24 Vdc |  | System
41 | Head Type |  |  |  | Standard |  |  | 84 | Output Signal |  | 4-20 mA Hart
42 | Head Material |  |  |  | Stainless Steel |  |  | 85
43 | Electical enclosure Class |  |  |  | IP 65 |  |  |  | CONFIGURATION
44 | Electrical Connections |  |  |  | M20 x 1.5 |  |  | 86 | Input Range Limits | °C | VTA | °C | - | VTA
45 | Terminal Block |  |  |  | Lead Wires |  |  | 87 | Factory Configuration |  | Yes
46 | Screw Cover / Chain |  |  |  | No |  |  | 88 | Factory Calibration |  | Yes
47 | Specific Span |  |  |  | -50 | - | 150 | 89
48 | [8 empty] | REQUIREMENTS AND TEST
49 | [7 empty] | 90 | NACE Requirments |  | No
| ACCESSORIES | [6 empty] | 91 | Hydro Test |  | Yes
50 | Sunshade |  |  |  | No |  |  | 92 | Material Certification |  | 3.1 Material Certificate
51 | Nipple |  |  |  | No |  |  | 93 | Test Requirements |  | Yes
52 | Chain |  |  |  | No |  |  | 94 | Factory Checking |  | Yes
53 | [7 empty] | 95 | Factory Calibration |  | N/A
54 | [7 empty] | 96 | PMI |  | No
55 | [7 empty] | 97 | NDE |  | Manufacturer's Standard
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  |  | WIKA |  |  | 104 | Note 1: Element and transmitter installed on same housing. Transmitter to be locally mounted attached on temperature element Note 2: Wake frequency calculation will be submitted by Vendor.
99 | Model Number |  |  |  | TIF50/TW10
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED