## Rev.
PAGE | REVISION | [6 empty] | PAGE | REVISION | [6 empty] | PAGE | REVISION
| 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | [7 empty] | 79 | [7 empty] | 157 | bar: REVISION 0
2 | [7 empty] | 80 | [7 empty] | 158 | bar: REVISION 0
3 | [7 empty] | 81 | [7 empty] | 159 | bar: REVISION 0
4 | [7 empty] | 82 | [7 empty] | 160 | bar: REVISION 0
5 | [7 empty] | 83 | [7 empty] | 161 | bar: REVISION 0
6 | [7 empty] | 84 | [7 empty] | 162
7 | [7 empty] | 85 | [7 empty] | 163
8 | [7 empty] | 86 | [7 empty] | 164
9 | [7 empty] | 87 | [7 empty] | 165
10 | [7 empty] | 88 | [7 empty] | 166
11 | [7 empty] | 89 | [7 empty] | 167
12 | [7 empty] | 90 | [7 empty] | 168
13 | [7 empty] | 91 | [7 empty] | 169
14 | [7 empty] | 92 | [7 empty] | 170
15 | [7 empty] | 93 | [7 empty] | 171
16 | [7 empty] | 94 | [7 empty] | 172
17 | [7 empty] | 95 | [7 empty] | 173
18 | [7 empty] | 96 | [7 empty] | 174
19 | [7 empty] | 97 | [7 empty] | 175
20 | [7 empty] | 98 | [7 empty] | 176
21 | [7 empty] | 99 | [7 empty] | 177
22 | [7 empty] | 100 | [7 empty] | 178
23 | [7 empty] | 101 | [7 empty] | 179
24 | [7 empty] | 102 | [7 empty] | 180
25 | [7 empty] | 103 | [7 empty] | 181
26 | [7 empty] | 104 | [7 empty] | 182
27 | [7 empty] | 105 | [7 empty] | 183
28 | [7 empty] | 106 | [7 empty] | 184
29 | [7 empty] | 107 | [7 empty] | 185
30 | [7 empty] | 108 | [7 empty] | 186
31 | [7 empty] | 109 | [7 empty] | 187
32 | [7 empty] | 110 | [7 empty] | 188
33 | [7 empty] | 111 | [7 empty] | 189
34 | [7 empty] | 112 | [7 empty] | 190
35 | [7 empty] | 113 | [7 empty] | 191
36 | [7 empty] | 114 | [7 empty] | 192
37 | [7 empty] | 115 | [7 empty] | 193
38 | [7 empty] | 116 | [7 empty] | 194
39 | [7 empty] | 117 | [7 empty] | 195
40 | [7 empty] | 118 | [7 empty] | 196
41 | [7 empty] | 119 | [7 empty] | 197
42 | [7 empty] | 120 | [7 empty] | 198
43 | [7 empty] | 121 | [7 empty] | 199
44 | [7 empty] | 122 | [7 empty] | 200
45 | [7 empty] | 123 | [7 empty] | 201
46 | [7 empty] | 124 | [7 empty] | 202
47 | [7 empty] | 125 | [7 empty] | 203
48 | [7 empty] | 126 | [7 empty] | 204
49 | [7 empty] | 127 | [7 empty] | 205
50 | [7 empty] | 128 | [7 empty] | 206
51 | [7 empty] | 129 | [7 empty] | 207
52 | [7 empty] | 130 | [7 empty] | 208
53 | [7 empty] | 131 | [7 empty] | 209
54 | [7 empty] | 132 | [7 empty] | 210
55 | [7 empty] | 133 | [7 empty] | 211
56 | [7 empty] | 134 | [7 empty] | 212
57 | [7 empty] | 135 | [7 empty] | 213
58 | [7 empty] | 136 | [7 empty] | 214
59 | [7 empty] | 137 | [7 empty] | 215
60 | [7 empty] | 138 | [7 empty] | 216
61 | [7 empty] | 139 | [7 empty] | 217
62 | [7 empty] | 140 | [7 empty] | 218
63 | [7 empty] | 141 | [7 empty] | 219
64 | [7 empty] | 142 | [7 empty] | 220
65 | [7 empty] | 143 | [7 empty] | 221
66 | [7 empty] | 144 | [7 empty] | 222
67 | [7 empty] | 145 | [7 empty] | 223
68 | [7 empty] | 146 | [7 empty] | 224
69 | [7 empty] | 147 | [7 empty] | 225
70 | [7 empty] | 148 | [7 empty] | 226
71 | [7 empty] | 149 | [7 empty] | 227
72 | [7 empty] | 150 | [7 empty] | Appendix
73 | [7 empty] | 151
74 | [7 empty] | 152 | [7 empty] | Att. 1
75 | [7 empty] | 153 | [7 empty] | Att. 2
76 | [7 empty] | 154 | [7 empty] | Att. 3
77 | [7 empty] | 155 | [7 empty] | Att. 4
78 | [7 empty] | 156 | [7 empty] | Att. 5

## INDEX 2
Item No | Inst_tag | Location | inst_desc | service | PID No. | Unit | Instrument Calibrated Range | Remarks
1 | PIT-RU0001A-01 | Compressor Skid | Pressure Transmitter | Compressor Suction pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 10.3
2 | PIT-RU0001A-03 | Compressor Skid | Pressure Transmitter | Discharge pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
3 | PIT-RU0001A-02 | Compressor Skid | Pressure Transmitter | Oil header Compressor pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
4 | PIT-RU0001A-05 | Compressor Skid | Pressure Transmitter | Upstream oil filter pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
5 | PIT-RU0001A-06 | Compressor Skid | Pressure Transmitter | Downstream oil filter pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
6 | PIT-RU0001A-04 | Compressor Skid | Pressure Transmitter | Pressure transmitter oil separator | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
7 | TIT-RU0001A-01 | Compressor Skid | Temperature Transmitter | Compressor Suction temperature transmitter | EI027-HSE-VD-PR-PID-002 | °C | -50.0 to 100
8 | TIT-RU0001A-03 | Compressor Skid | Temperature Transmitter | Oil Separator temperature transmitter | EI027-HSE-VD-PR-PID-002 | °C | -50.0 to 100
9 | TIT-RU0001A-02 | Compressor Skid | Temperature Transmitter | Oil header compressor temperature transmitter | EI027-HSE-VD-PR-PID-002 | °C | -50.0 to 100
10 | ZE-RU0001A-01 | Compressor Skid | Position Sensor | Compressor slide valve position Sensor | EI027-HSE-VD-PR-PID-002 | % | 0.0 to 100.0
11 | LIT-RU0001A-01 | Chiller Skid | Level Transmitter | Chiller level transmitter | EI027-HSE-VD-PR-PID-002 | % | 0.0 to 100.0
12 | LV-RU0001A-01 | Chiller Skid | Level Control Valve | Chiller level control valve | EI027-HSE-VD-PR-PID-002 | % | 0.0 to 100.0
13 | SOV-RU0001A-01D | Compressor Skid | Solenoid Valve | Compressor capacity load Return solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
14 | SOV-RU0001A-01A | Compressor Skid | Solenoid Valve | Compressor capacity unload supply solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
15 | SOV-RU0001A-01C | Compressor Skid | Solenoid Valve | Compressor capacity load supply solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
16 | SOV-RU0001A-01E | Compressor Skid | Solenoid Valve | Compressor capacity unload Return solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
17 | SOV-RU0001A-03 | Chiller Skid | Solenoid Valve | Hot gas solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
18 | SOV-RU0001A-02 | Chiller Skid | Solenoid Valve | Evaporator oil drain line. | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
19 | TS-RU0001A-01A | Electrical Heater | Temperature Switch | Oil heater temp. control switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
20 | TS-RU0001A-01B | Electrical Heater | Temperature Switch | Oil heater Surface and box temp. control switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
21 | LS-RU0001A-01 | Compressor Skid | Level Switch | Oil separator level switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
22 | VS-RU0001A-01A | Chiller Skid | Vibration Switch | Air Cooler motor 2 vibration switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
23 | VS-RU0001A-01B | Chiller Skid | Vibration Switch | Air Cooler motor 3 vibration switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
24 | PSV-RU0001A-03 | Chiller Skid | Pressure safety valve | Evaporator Safety Valve | EI027-HSE-VD-PR-PID-002
25 | PSV-RU0001A-02 | Chiller Skid | Pressure safety valve | Receiver Safety Valve | EI027-HSE-VD-PR-PID-002
26 | LG-RU0001A-02 | Chiller Skid | Level Gauge | Receiver Level Gauge | EI027-HSE-VD-PR-PID-002
27 | PG-RU0001A-01 | Compressor Skid | Pressure gauge | Compressor Suction pressure gauge | EI027-HSE-VD-PR-PID-002
28 | PIT-RU0001B-01 | Compressor Skid | Pressure Transmitter | Compressor Suction pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 10.3
29 | PIT-RU0001B-03 | Compressor Skid | Pressure Transmitter | Discharge pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
30 | PIT-RU0001B-02 | Compressor Skid | Pressure Transmitter | Oil header Compressor pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
31 | PIT-RU0001B-05 | Compressor Skid | Pressure Transmitter | Upstream oil filter pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
32 | PIT-RU0001B-06 | Compressor Skid | Pressure Transmitter | Downstream oil filter pressure transmitter | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
33 | PIT-RU0001B-04 | Compressor Skid | Pressure Transmitter | Pressure transmitter oil separator | EI027-HSE-VD-PR-PID-002 | barG | -1.0 to 27.6
34 | TIT-RU0001B-01 | Compressor Skid | Temperature Transmitter | Compressor Suction temperature transmitter | EI027-HSE-VD-PR-PID-002 | °C | -50.0 to 100
35 | TIT-RU0001B-03 | Compressor Skid | Temperature Transmitter | Oil Separator temperature transmitter | EI027-HSE-VD-PR-PID-002 | °C | -50.0 to 100
36 | TIT-RU0001B-02 | Compressor Skid | Temperature Transmitter | Oil header compressor temperature transmitter | EI027-HSE-VD-PR-PID-002 | °C | -50.0 to 100
37 | ZE-RU0001B-01 | Compressor Skid | Position Sensor | Compressor slide valve position Sensor | EI027-HSE-VD-PR-PID-002 | % | 0.0 to 100.0
38 | LIT-RU0001B-01 | Chiller Skid | Level Transmitter | Chiller level transmitter | EI027-HSE-VD-PR-PID-002 | % | 0.0 to 100.0
39 | LV-RU0001B-01 | Chiller Skid | Level Control Valve | Chiller level control valve | EI027-HSE-VD-PR-PID-002 | % | 0.0 to 100.0
40 | SOV-RU0001B-01D | Compressor Skid | Solenoid Valve | Compressor capacity load Return solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
41 | SOV-RU0001B-01A | Compressor Skid | Solenoid Valve | Compressor capacity unload supply solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
42 | SOV-RU0001B-01C | Compressor Skid | Solenoid Valve | Compressor capacity load supply solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
43 | SOV-RU0001B-01E | Compressor Skid | Solenoid Valve | Compressor capacity unload Return solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
44 | SOV-RU0001B-03 | Chiller Skid | Solenoid Valve | Hot gas solenoid valve | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
45 | SOV-RU0001B-02 | Chiller Skid | Solenoid Valve | Evaporator oil drain line. | EI027-HSE-VD-PR-PID-002 |  | 1 = Energized
46 | TS-RU0001B-01A | Electrical Heater | Temperature Switch | Oil heater temp. control switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
47 | TS-RU0001B-01B | Electrical Heater | Temperature Switch | Oil heater Surface and box temp. control switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
48 | LS-RU0001B-01 | Compressor Skid | Level Switch | Oil separator level switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
49 | VS-RU0001B-01A | Chiller Skid | Vibration Switch | Air Cooler motor 2 vibration switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
50 | VS-RU0001B-01B | Chiller Skid | Vibration Switch | Air Cooler motor 3 vibration switch | EI027-HSE-VD-PR-PID-002 |  | Dry Contact
51 | PSV-RU0001B-03 | Chiller Skid | Pressure safety valve | Evaporator Safety Valve | EI027-HSE-VD-PR-PID-002
52 | PSV-RU0001B-02 | Chiller Skid | Pressure safety valve | Receiver Safety Valve | EI027-HSE-VD-PR-PID-002
53 | LG-RU0001B-02 | Chiller Skid | Level Gauge | Receiver Level Gauge | EI027-HSE-VD-PR-PID-002
54 | PG-RU0001B-01 | Compressor Skid | Pressure gauge | Compressor Suction pressure gauge | EI027-HSE-VD-PR-PID-002
Alarm