## PG-RU0001AB-01
#REF!
#REF!
#REF! |  |  |  | #REF! | [6 empty] | Page: 3
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PG-RU0001A-01,PG-RU0001B-01 | [5 empty] | 7 | AREA Classification | Zone 2 IIB T3
2 | Service | Compressor Suction | [5 empty] | 8
3 | Line No. | 6"-PR-RU0001(A/B)01-ML3R1-C | [5 empty] | 9
4 | Line Size | Line Schedule |  | 6" |  |  |  | 10
5 | Equipment No. | [6 empty] | 11
6 | PID No. | [6 empty] | 12
| GAUGE/SENSING ELEMENT | [7 empty] | DIAPHRAGM SEAL
13 | Type |  |  | Direct Reading |  |  |  | 56 | Seal Type | Without Seal
14 | Instrument Range bar G |  |  | -1 |  | - | 24 | 57 | Process Connection | -
15 | Dial Size |  |  | 100 mm |  |  |  | 58 | Diaphragm seal | -
16 | Dial Color |  |  | Black Labels-White Background |  |  |  | 59 | Top Housing Material | -
17 | Case Material |  |  | 316 SS |  |  |  | 60 | Bottom Housing Material | -
18 | Mounting |  |  | Direct installation |  |  |  | 61 | Fill Fluid | -
19 | Window Material |  |  | Safety Glass |  |  |  | 62 | Capillary Length | -
20 | Zero Adjustment |  |  | External |  |  |  | 63 | Capillary Material | -
21 | Span Adjustment |  |  | Internal |  |  |  | 64 | Flushing Connection | -
22 | Nominal Accuracy |  |  | Class 1.0 |  |  |  | 65 | Connection to Instrument | -
23 | Element Type |  |  | Bourdon |  |  |  | 66
24 | Pressure Element Material |  |  | 316L SS |  |  |  | 67
25 | Movement Material |  |  | 316 SS |  |  |  | 68
26 | Connection Size |  |  | 1/2" NPTM |  |  |  |  | ACCESSORIES
27 | Connection Material |  |  | 316L SS |  |  |  | 69 | Accessories Code | Other
28 | Connection Location |  |  | Radial Bottom |  |  |  | 70 | Overrange Protection | Without Accessories
29 | Process Connection Type |  |  | Threaded |  |  |  | 71 | Pulsation Damper/Snubber | No
30 | Blow-Out Protection |  |  | Yes |  |  |  | 72 | Damper Material | -
31 | Case Liquid Filling |  |  | GLYCERINE FILLED |  |  |  | 73 | Shypon | No
32 | Overpressure |  |  | Yes, 1.5 times the full scale pressure |  |  |  | 74 | Shypon Material | -
33 | Solid Front |  |  | Yes |  |  |  | 75 | Manifold Type | 2- Valve manifold
34 | Weather Protection |  |  | IP65 |  |  |  | 76 | Manifold Material | 316 SS
35 | [7 empty] | 77 | Manifold Process Connection | 1/2" NPT Female-1/2" NPT Male
36 | [7 empty] | 78 | Mounting
37 | [7 empty] | 79
38 | [7 empty] | 80
39 | [7 empty] | 81
40 | [7 empty] | 82
41 | [7 empty] | 83
| PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
42 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments | No
43 | Phase Fluid |  |  | Vapor |  |  |  | 85 | ASME U STAMP Required | No
44 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification | 3.1 Material Certificate
45 | Pressure (Upstream) |  | bar A |  | 4.7 |  |  | 87 | Test Requirements | Yes
46 | Temperature |  | °C |  | -0.07 |  |  | 88 | Hydraulic test (accessories) | Yes
47 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration | Yes
48 | Toxic Agents |  |  | - |  |  |  | 90
49 | Design Pressure Min / Max |  | bar A | FV |  | 23 |  | 91
50 | Design Temp. Min / Max |  | °C | -45 |  | 120 |  | 92
51 | [7 empty] | 93
52 | [7 empty] | 94
53 | [7 empty] | 95
54 | [7 empty] | 96
55 | [7 empty] | 97
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | Wika |  |  |  | 104
99 | Model Number |  |  | 233.30
102 | Purchase Order No.
103 | Item Number