## PIT-RU0001AB-01
#REF!
#REF!
#REF! |  |  |  | #REF! | [8 empty] | Page: 3
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PIT-RU0001A-01,PIT-RU0001B-01 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Compressor Suction | [5 empty] | 8
3 | Line No. | 5"-PR-RU0001(A/B)01-ML3R1-C | [5 empty] | 9
4 | Line Size | Line Schedule |  | 5" |  |  |  | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | [6 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 10.3
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPT Female
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Gas |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 4.65 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | -0.17 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | PROPANE |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G | FV | 22 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -45 | 120 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-02
#REF!
#REF!
#REF! |  |  |  | #REF! | [8 empty] | Page: 4
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PIT-RU0001A-02,PIT-RU0001B-02 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Compressor Lubricant Inlet | [5 empty] | 8
3 | Line No. | 2"-OI-RU0001A05-MS3R0-E | [5 empty] | 9
4 | Line Size | Line Schedule |  | 2" |  |  |  | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | [6 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | Lubricant Oil |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Liquid |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 22.5 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 60 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 26 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-03
#REF!
#REF!
#REF! |  |  |  | #REF! | [8 empty] | Page: 7
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PIT-RU0001A-03,PIT-RU0001B-03 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Separator | [5 empty] | 8
3 | Line No. | [6 empty] | 9
4 | Line Size | Line Schedule | [5 empty] | 10
5 | Equipment No. | [6 empty] | 11
6 | PID No. | [6 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Gas |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 20.2 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 73.5 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-04
#REF!
#REF!
#REF! |  |  |  | #REF! | [8 empty] | Page: 8
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PIT-RU0001A-04,PIT-RU0001B-04 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Separator | [5 empty] | 8
3 | Line No. | [6 empty] | 9
4 | Line Size | Line Schedule | [5 empty] | 10
5 | Equipment No. | RU0001(A/B)-D-01 | [5 empty] | 11
6 | PID No. | [6 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | PROPANE |  |  |  | 84 | NACE Requirments |  |  | Yes
44 | Phase Fluid |  |  | Gas |  |  |  | 85 | ASME UV STAMP Required |  |  | -
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 19.8 |  |  | 87 | Test Requirements |  |  | Yes
47 | Temperature |  | °C |  | 73.5 |  |  | 88 | Factory Configuration |  |  | 2 Valve
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | 316 SS
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | 1/2" - NPTF
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE |  |  | -
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | No
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-05
#REF!
#REF!
#REF! |  |  |  | #REF! | [8 empty] | Page: 11
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PIT-RU0001A-05,PIT-RU0001B-05 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Cooler Discharge | [5 empty] | 8
3 | Line No. | 2"-0I-RU0001(A/B)02-MC3R1-E | [5 empty] | 9
4 | Line Size | Line Schedule |  | 2" |  |  |  | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | [6 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | Oil |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Liquid |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 19.7 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 60 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## PIT-RU0001AB-06
#REF!
#REF!
#REF! |  |  |  | #REF! | [8 empty] | Page: 12
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | PIT-RU0001A-06,PIT-RU0001B-06 | [5 empty] | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Pump Suction | [5 empty] | 8
3 | Line No. | 2"-0I-68003A-MS3R0-E | [5 empty] | 9
4 | Line Size | Line Schedule | [5 empty] | 10
5 | Equipment No. | - | [5 empty] | 11
6 | PID No. | [6 empty] | 12
| TRANSMITTER BODY | [7 empty] | BASIS AND SELECTION
13 | Instrument Function |  |  | Gauge Pressure |  |  |  | 55 | Mounting |  |  | Bracket for 2" pipe
14 | Element Type |  |  | Pressure Cell |  |  |  | 56 | Power Supply From |  |  | 24 Vdc |  | System
15 | Element Material |  |  | Stainless Steel & Hastelloy |  |  |  | 57 | Accuracy % | Repeatibility |  | ±0.2% F.S
16 | Body Material |  |  | Stainless Steel |  |  |  | 58 | Output signal |  |  | 4-20 mA Hart
17 | Material Detail |  |  | 316L SST |  |  |  | 59 | Electrical Protection |  |  | IP 65
18 | Body Rating |  |  | - |  |  |  | 60 | IP Rating |  |  | Ex ia IIB T3
19 | Overrange Protection |  |  | 130% of Range |  |  |  | 61 | Zero Adjustment |  |  | External
20 | Vent | Drain |  | Yes |  | No |  | 62 | Electrical Connections |  |  | M20 x 1.5
21 | Fill Fluid |  |  | Silicone Oil |  |  |  | 63 | Span Adjustable |  |  | External
22 | Wetted O-Rings Material |  |  | Teflon-coated 316L |  |  |  | 64 | Calibrated Range |  | bar G | -1 |  | - | 27.6
23 | Bolts Material |  |  | Stainless Steel |  |  |  | 65 | Instrument Range |  | bar G | -1 |  | - | 40
24 | Housing Material |  |  | Die-Cast AL |  |  |  | 66
25 | Process Connection |  |  | 1/2" - NPTM |  |  |  | 67
26 | [7 empty] | 68
27 | [7 empty] | 69
28 | [7 empty] | 70
29 | [7 empty] | 71
30 | DIAPHRAGM SEALS | [7 empty] | ACCESSORIES
31 | Seal | Type |  | No | Without Seal |  |  | 72 | Indicator |  |  | Yes
32 | Flange Size / Rating | [6 empty] | 73 | Integral Meter Scale |  |  | -
33 | Flange Facing / Finish | [6 empty] | 74 | Mounting Bracket |  |  | Yes
34 | Capillary Type / Length | [6 empty] | 75 | Integral Manifold |  |  | Yes
35 | Capillary Material | [6 empty] | 76 | Manifold Type |  |  | 2 Valve
36 | Fill Fluid | [6 empty] | 77 | Manifold Material |  |  | 316 SS
37 | Flushing Connection | [6 empty] | 78 | Manifold Process Connection |  |  | 1/2" - NPTF
38 | Diaphragm Material | [6 empty] | 79 | Manifold Model |  |  | VTA
39 | Model | [6 empty] | 80 | Sunshade |  |  | No
40 | Process Connection | [6 empty] | 81
41 | Upper Housing Material | [6 empty] | 82
| Lower Housing Material | [6 empty] | 83
42 | PROCESS DATA | [7 empty] | REQUIREMENTS AND TEST
43 | Fluid |  |  | Oil |  |  |  | 84 | NACE Requirments |  |  | No
44 | Phase Fluid |  |  | Liquid |  |  |  | 85 | ASME UV STAMP Required |  |  | No
45 | Operating Conditions |  |  | Min | Norm |  | Max | 86 | Material Certification |  |  | Yes
46 | Pressure (Upstream) |  | bar A |  | 19.7 |  |  | 87 | Test Requirements |  |  | -
47 | Temperature |  | °C |  | 60 |  |  | 88 | Factory Configuration |  |  | Yes
48 | Corrosive Agents |  |  | - |  |  |  | 89 | Factory Calibration |  |  | Yes
49 | Toxic Agents |  |  | - |  |  |  | 90 | SIL Requirements |  |  | -
50 | Design Pressure Min / Max |  | bar G |  | 22 |  |  | 91 | NDE |  |  | -
51 | Design Temp. Min / Max |  | °C | -29 | 100 |  |  | 92 | Hydro Test |  |  | 1.5 times of scaled range
52 | [7 empty] | 93
53 | [7 empty] | 94
54 | [7 empty] | 95
55 | [7 empty] | 96
| PURCHASE DATA | [7 empty] | NOTES
98 | Manufacturer |  |  | WIKA |  |  |  | 104
99 | Model Number |  |  | IPT-20
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED