INSPECTION & TEST PLAN FOR SHELL AND TUBE HEAT EXCHANGER

Tabulation of Revised Pages

| Page | Revision |  |  |  |  |  |  |  | Page | Revision |  |  |  |  |  |  |  | Page | Revision |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 00 | 01 | 02 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 23 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 24 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 | Χ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table of Contents

1.	Purpose	4

2.	Applicable Documents	4

3.	Definitions	4

3.1	General definitions	4

3.2	Abbreviations	5

4.	General Requirements	5

5.	Definition of CONTRACTOR and CLIENT / TPI Involvement	5

6.	VENDOR’s Quality Manual and Quality Control Plan (VQCP)	6

7.	Inspection Activities	7

8.	Attachments	7

8.1	Attachment #1: ITP for Shell and Tube Heat Exchanger (3 Sheets)	7

8.2	Attachment #2: Test Sequence Standards with reference to TEMA Type of Shell and Tube Heat Exchangers (13 Sheets)	7

# Purpose

The inspection and test plan is an engineering document, which defines the type and extent of CONTRACTOR and CLIENT involvement in each phase of fabrication, control and testing requirements and inspection.

The inspection and test plan may under no circumstances be used as a substitute for the VENDOR's Quality Manual and/or Quality Control Plan. The VENDOR shall in any case conduct all the tests required by contractual documents, specifications, codes and standards, and keep the relevant documentation.

CONTRACTOR and CLIENT shall be entitled to send their inspectors to attend inspection in the VENDOR’s workshop.

This inspection and test plan shall be used as a basis for the definition of the material inspection plan during pre-inspection meeting.

# Applicable Documents

| ASME Sec. II | Material |
| --- | --- |
| ASME Sec. VIII Div. 1 | Rules for Construction of Pressure Vessels |
| ASME Sec. VIII Div. 2 | Rules for Construction of Pressure Vessels, Alternative Rules |
| ASME Sec .V | Non-Destructive Examination |
| ASME Sec. IX | Welding and Brazing Qualifications |
| TEMA Standard | Tubular Exchanger Manufacturers Associations |
| API 660 | Shell & Tube Heat Exchangers |
| BS EN 10204 (3.1) | Material Certificates |
| All Standards and Specifications listed in the Requisition |  |

# Definitions

## General definitions

| Site | The lands and other places in or through which the works provided by the OWNER for the purpose of the CONSTRUCTION CONTRACT |
| --- | --- |
| Shall | Mandatory requirements |
| Should | Recommended or advisory requirements |
| May | Optional |
| Approved | Approved by OWNER |

## Abbreviations

| Abbreviation | Meaning |
| --- | --- |
| NDT | None Destructive Test |
| WPS/PQR | Welding Procedure Specification/Procedure Qualification Record |
| VQCP | Vendor’s Quality Manual and Quality Control Plan |
| ITP | Inspection and Test Plan |
| TPI | Third Party Inspector |
| PIM | Pre Inspection Meeting |

# General Requirements

The VENDOR shall inspect all the manufactured items to ensure that materials and workmanship are in accordance with applicable codes, standards and specifications indicated in the relevant Purchase Order.

All the manufactured items shall be inspected according to CONTRACTOR’S requirements. However, the acceptance of any work and/or release of them by the CONTRACTOR shall in no way relieve the VENDOR of any responsibility for carrying out all the provisions of the codes and specifications.

The CONTRACTOR and CLIENT or their authorized Inspectors/Representatives shall have free access at all reasonable time to all shops of the VENDOR or Sub-VENDOR for inspection/witnessing of work.

# Definition of CONTRACTOR and CLIENT / TPI Involvement

The nature of CONTRACTOR and CLIENT involvement is indicated against each activity of fabrication and testing by means of the letters H, W, SW, R and A with the following definitions:

H: (Hold) Point

The VENDOR cannot carry out the specified controls and tests without CONTRACTOR and CLIENT attendance and witnessing. The VENDOR must notify CONTRACTOR by fax of the dedicated inspection activity at least twenty (20) Calendar days in advance and consequently CLIENT will be informed by CONTARACTOR. The VENDOR cannot deviate from this rule unless written approval has been given by CONTRACTOR.

W:(Witness)

The VENDOR must notify CONTRACTOR of the dedicated inspection activity at least twenty (20) Calendar days in advance and consequently CLIENT will be informed by CONTARACTOR. Although CONTRACTOR and CLIENT witnessing is not mandatory.

If CONTRACTOR does not elect to be present, the VENDOR may proceed with his own inspection, provided controls and test records are made available to CONTRACTOR for review.

SW: (Spot Witness)

Spot Witness denotes to random attendance of inspector without any invitation from the VENDOR and without advance notification by the CONTRACTOR to the VENDOR.

R: (Review) – Review of Documents

The VENDOR has either to submit to CONTRACTOR for review and comments the documents required prior to the performance of the dedicated activity or to transmit or make available for the review of CONTRACTOR the result of the controls and tests conducted, as the case may be. Consequently CLIENT will be informed by CONTARACTOR.

A: (Approval) – Approval of Documents

The VENDOR has either to submit to CONTRACTOR for comments and approvals the documents required prior to the performance of the dedicated activity or to transmit or make available for the approval of CONTRACTOR the result of the controls and tests conducted, as the case may be. VENDOR is not allowed to proceed the work before receipt of CONTRACTOR approval on the required documents.

Levels of Inspection:

Inspection levels shall be based on the criticality and complexity of the equipment, as determined by engineering.

Level 1: Full scope inspection

In addition to the visits required for formal witness points, the inspector shall visit the VENDOR on a regular basis to monitor work in progress. The frequency of visits will depend on the complexity and size on the order and the quality history of the VENDOR.

Level 1*: Modified Full scope inspection

The visits required for formal witness points are to be performed.

Level 2: Limited Scope Inspection

The inspector shall visit the VENDOR to inspect a limited number of pre-determined witness points.

Level 3: Final inspection prior to Shipment

The inspector shall provide specific instructions to the VENDOR defining the activities to be witnessed or the details to be verified.

Level 4: No source inspection required.

The inspector shall review and accept VENDOR’s certifications, test reports and QC data book documentation.

Level of inspection for this particular ITP is considered as level ‘1’ or ‘1*’.  Level of inspection of Long Lead Items are exception and in any case are being treated as level ‘1’.

# VENDOR’s Quality Manual and Quality Control Plan (VQCP)

The VENDOR’s Quality Control Plan is a document, which defines in a chronological manner the list of the operations, controls and tests in accordance with his own “know-how” and with the requirements specified in CONTRACTOR’s requisition.

The VENDOR must issue a Quality Control Plan for each type or category of material and component and the following information shall be clearly specified against each operation:

Reference documents (drawings, procedures, etc …)

Acceptance criteria (code, etc …)

Recording documents for control and tests.

Involvement of the Quality Control department of the VENDOR and/or his Sub-VENDOR.

The VQCP will have to include all CONTRACTOR and CLIENT inspection activities defined in inspection and test plan as well as all inspection activities scheduled by the third party inspection company.

For component of inspection levels 1 and 2 the VENDOR’s VQCP shall be submitted compulsorily to CONTRACTOR and CLIENT for comments before the Pre-Inspection Meeting or starting the manufacturing. Vendor’s Quality Manual shall also be submitted to CONTRACTOR upon request.

# Inspection Activities

For detail of inspection activities, see relevant inspection and test plan in attachment # 1 as minimum requirements which shall be finalized during PIM.

# Attachments

## Attachment #1: ITP for Shell and Tube Heat Exchanger (3 Sheets)

## Attachment #2: Test Sequence Standards with reference to TEMA Type of Shell and Tube Heat Exchangers (13 Sheets)

Attachment # 1

ITP for Shell and Tube Heat Exchanger

(3 Sheets)

Table: Inspection Activities

| INSPECTION ACTIVITIES | APPLICABLE DOCUMENTS | CONTRACTOR | CLIENT / TPI |
| --- | --- | --- | --- |
| VENDOR’s Quality Control Plan | VENDOR’s Document | R | R |
| Pre-Inspection Meeting | Agenda | H | H |
| Material Test Certificate | BS EN 10204 (3.1) | R | R |
| Checking The Material With Requirements of Requisition | Requisition | W | W |
| Inspection of Sub Ordered Components | Requisition | W | W |
| Material identifications and markings | VENDOR’s Approved Procedure | W | W |
| Storage of materials and welding consumables | VENDOR’s Approved Procedure | R | R |
| WPS/PQR | Design Code, ASME Sec IX | R/A | R |
| Welder’s Qualifications (Note 1) | ASME Sec. IX | R/A | R |
| NDT Personnel’s Qualification | Design Code, ASME Sec V, ASNT Lev.II or eqv. | R/A | R |
| Material Traceability | VENDOR’s Approved Procedure | W | W |
| Dimensional check (before forming & rolling) | Approved Drawings | W | W |
| Cutting, Forming, Rolling, Punching, Drilling, Tacking and Fit up | Approved Drawings | W | W |
| Inspection of Back Gouged portions of edges prepared for welding by MT or PT | Design Code, ASME Sec V | W | W |
| Tube Expanding / Tube to tubesheet Welding | Approved Drawings | W | W |
| Tube to Tubesheet joint test (Notes 5) | Approved Procedure | W | W |
| Welding | Design Code, ASME Sec IX | W | R |
| Bundle Assembly | Approved Drawings | W | R |
| Confirmation of NDT Results VT, RT, UT, MT, PT (Review of all Radiographs) | Design Code, ASME Sec V | W/A | R |
| Preparation of Production Test Plate | Requisition | W | R |
| Mechanical Testing of Production Test Plate | ASME Sec II, Requisition | W | R |
| Chemical Analysis of Production Test Plate | ASME Sec II, Requisition | W | R |
| Execution of Major Repair | Requisition | W | W |
| Completeness check | Approved Drawings | H | H |
| PWHT/ Stress Relieve (Note 2) | Design Code | R/A | R |
| NDTafter PWHT/ Stress Relieve | Requisition | R/A | R |
| Roughness checking (Flange Facing, Internal Surface, etc.) | Approved Drawings | W | R |
| Confirmation of Hardness Measurement in Final Condition, if applicable | Design Code, ASME Sec V | W | R |
| Final Visual and Dimensional Check | Approved Drawings and Standards | H | W |
| Reinforcing Pad air-soap test | Requisition | W | W |
| Leakage Test/Hydrotest | Requisition | H | H |
| Complete Draining and drying, N2/VPT/desiccant filling, (which applicable) | Requisition | W | W |
| Surface Preparation, Anti-Corrosion / Painting | Requisition | W | W |
| Pickling & Passivation (where applicable) | Requisition | W | W |
| Name plate, Cleanliness, Tagging and Marking | Requisition | W | W |
| Auxiliary Items (Spare Parts, Bolts, Nuts, etc.) | Requisition | W | W |
| Packing / Preparation for Shipment | Requisition | W | W |
| Check Identification and Destination Marking | Requisition | W | R |
| Pre Shipment Inspection (PSI) Including Packing, Marking and Review of Documents | Requisition | H | H |
| Non Conformities Treatment | Requisition | W | W |
| NDT Documents | Design Code, ASME Sec V | R/A | R |
| Documentations | Requisition | A | W/R |
| Control of Packing List | - | H | W |
| Deviations | - | H | W/R |
| Final Inspection / Data Book | Requisition | H/A | W/R |
| Release Note | - | H | H |

| Notes: |  |
| --- | --- |
| 1- | If Inspector doubts welder’s ability, Inspector may request Welder for new qualification test. |
| 2- | Inspector has right to request VENDOR to witness if he/she deems necessary. |
| 3- | All shop tests shall be done by VENDOR or his SUB-VENDOR. |
| 4- | Qualification of sub-VENDORs shall be approved by CONTRACTOR. |
| 5- | For lethal / toxic services: Hold Point of CONTRACTOR to be considered. |

Attachment # 2

Test Sequence Standards with reference to TEMA Type of Shell and Tube Heat Exchangers

(13 Sheets)

Hydrostatic test procedure and test ring requirement for Shell and Tube Heat Exchangers:  U tube, Floating head and Fixed Tubesheet are as specified sketches.

Fig. 1-1 : Standard for Floating Head Exchangers Case 1- Shell pressure ≥ bundle pressure Tests made : Figs 1,3,4 Elements tested: Fig. 1 - Extra tubular space a.; Tube to tube-sheet joints. b.; Tube failure. Fig 3 - Test of removable head g.; Channel. h.; Gasket between channel and channel cover. f.; Gasket between channel and tube-sheet. d.; Floating head cover to tube-sheet. Fig 4 - Test of shell j.; Gasket between shell cover and shell. l.; Gasket between channel and tube-sheet. c.; Shell + cover. Case 2- bundle pressure > shell pressure. Test made: Figs. 1 (Note 1), 2,3,4. Elements tested:. Fig. 1 - See Case 1. Fig. 2 - Intratubular space. a.; Tube to tube-sheet joints. b.; Tube failure.. Fig. 3 - See Case 1. Fig. 4 - See Case 1. Notes:. (1) This test is made only when the tubes are welded. to the tube-sheet.. (2) For tubes welded to the tube-sheet, a dye-penetrant. examination or test with ammonia must be. conducted before and after the hydraulic test to. locate any cracking..

Fig. 1-2: Standard for Floating Head Exchangers (Continued) Case 1- Shell pressure ≥ bundle pressure Tests made : Figs 1,3,4 Elements tested: Fig. 1 - Extra tubular space a.; Tube to tube-sheet joints. b.; Tube failure. Fig 3 - Test of channel and floating head c.; Channel. d.; Gasket between channel and channel cover. e.; Gasket between channel and tube-sheet. Fig 4 - Test of shell cover f.; Gasket between shell cover and shell. g; Gasket between channel and tube-sheet. h.; Shell + cover. Case 2- bundle pressure > shell pressure. Test made: Figs. 1 (as per floating head 1), 2,3,4. Elements tested:. Fig. 1 - See Case 1. Fig. 2 - Intratubular space. a.; Tube to tube-sheet joints. b.; Tube failure.. Fig. 3 - See Case 1. Fig. 4 - See Case 1. Notes:. (1) For tubes welded to the tube-sheet, a dye-penetrant. examination or test with ammonia must be. conducted before and after the hydraulic test to. locate any cracking..

Case 1- Shell pressure ≥ bundle pressure Tests made : Figs 1,3,4 Elements tested: Fig. 1 - Extra tubular space a.; Tube to tube-sheet joints. b.; Tube failure. Fig 3 - Test of channel and floating end g.; Channel and floating end. h.; Gasket between channel and channel cover. f.; Gasket between channel and tube-sheet. Fig 4 - Test of shell cover j.; Gasket between shell cover and shell. k.; Gasket between channel and tube-sheet. l.; Shell + cover. Case 2- bundle pressure > shell pressure. Test made: Figs. 1 (Note 1), 2,3,4. Elements tested:. Fig. 1 - See Case 1. Fig. 2 - Intratubular space. a.; Tube to tube-sheet joints. b.; Tube failure.. Fig. 3 - See Case 1. Fig. 4 - See Case 1. Notes:. (1) This test is made only when the tubes are welded. to the tube-sheet.. (2) For tubes welded to the tube-sheet, a dye-penetrant. examination or test with ammonia must be. conducted before and after the hydraulic test to. locate any cracking.. Fig. 1-3: Standard for Floating Head Exchangers (Continued)

Case 1- Shell pressure ≥ bundle pressure

Tests made : Figs 2,4 (Note 1)

Elements tested:

Fig. 2 - Intratubular space

| a. | Tube to tube-sheet joints |  |
| --- | --- | --- |
| b. | Tube failure |
| c. | Gasket of floating head |
| d. | Gasket of channel |
| e. | Test of channel and floating head |

Fig 4 - Test of shell and shell cover

| f. | Gasket between shell and channel |  |  |  |
| --- | --- | --- | --- | --- |
| g. | Shell |  |  |  |
| h. | Shell cover |  |  |  |
| j. | Gasket between channel and tube-sheet |  |  |  |

| Case 2- bundle pressure > shell pressure |  |  |  |  |
| --- | --- | --- | --- | --- |
| Test made: Figs. 1,3,4 |  |  |  |
| Elements tested: |  |  |
| Fig. 1 – Extra tublar space |  |  |
| a.; Tube to tube-sheet joints. b.; Tube failure. |
| Fig. 3 - Intratubular space |  |  |  |
| c.; Gasket of floating head. d.; Gasket between channel and channel cover. e.; Channel and floating head. |
| Fig. 4 – Test of shell and shell cover : See Case 1 |  |  |
| Notes: |  |
| (1) Test 1 is made only when the tubes are welded |  |  |  |  |
| to the tube-sheet. |  |  |
| (2) Provide blind nuts and gaskets for floating tubesheet (3) For tubes welded to the tube-sheet, a dye-penetrant |  |  |  |  |
| examination or test with ammonia must be |  |  |  |  |
| conducted before and after figures 1 or 2 tests to check and locate any cracking. |  |  |  |  |

Fig. 1-4: Standard for Floating Head Exchangers (Continued)

Fig. 1-5: Standard for Floating Head Exchangers (Continued)

| In all cases: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Tests made : Figs. 1,2,3 |  |  |  |  |  |
| Elements tested: |  |  |  |  |
| Fig. 1 - Extra tubular space |  |  |  |  |  |
| a. |  | Tube to tube-sheet joints |  |  |  |  |
| b. |  | Tube failure |  |  |  |
| c. |  | Floating head and gasket |  |  |  |  |
| Fig 2 - Extra tubular space |  |  |  |  |  |
| d. |  |  | Shell |  |
| e. |  |  | Gasket between shell and tube-sheet |  |  |  |  |
| Fig 3 - Test of channel |  |  |  |  |  |
| f. | Gasket between channel cover and channel |  |  |  |  |  |  |
|  | Gasket between channel and tube-sheet |  |  |  |  |  |  |
| g. | Test of channel |  |  |  |  |
| Notes: |  |  |  |  |
| - If the shell pressure is higher than the channel Pressure, continue test 1 to the |  |  |  |  |  |  |  |
| shell pressure if possible so as to check |  |  |  |  |  |  |  |
| a, b and c. |  |  |  |  |  |  |
| (2) For tubes welded to the tube-sheet, a dye- |  |  |  |  |  |  |  |
| penetrant examination or test with ammonia |  |  |  |  |  |  |  |
| must be conducted before figure 1 test and |  |  |  |  |  |  |  |
| after figure 2 test to check the welds and. |  |  |  |  |  |  |  |

locate any cracks.

| In all cases: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Tests made : Figs. 1,2,3 |  |  |  |  |  |
| Elements tested: |  |  |  |  |
| Fig. 1 - Extra tubular space |  |  |  |  |  |
| a. |  | Tube to tube-sheet joints |  |  |  |  |
| b. |  | Tube failure |  |  |  |
| c. |  | Floating head and gasket |  |  |  |  |
| Fig 2 - Extra tubular space |  |  |  |  |  |
| d. |  |  | Shell |  |
| e. |  |  | Gasket between shell and tube-sheet |  |  |  |  |
| Fig 3 - Test of channel |  |  |  |  |  |
| f. | Gasket between channel cover and channel |  |  |  |  |  |  |
|  | Gasket between channel and tube-sheet |  |  |  |  |  |  |
| g. | Test of channel |  |  |  |  |
| Notes: |  |  |  |  |
| - If the shell pressure is higher than the channel pressure, continue test 1 to the |  |  |  |  |  |  |  |
| shell pressure if possible so as to check |  |  |  |  |  |  |  |
| a, b and c. |  |  |  |  |  |  |
| (2) For tubes welded to the tube-sheet, a dye- |  |  |  |  |  |  |  |
| penetrant examination or test with ammonia |  |  |  |  |  |  |  |
| must be conducted before figure 1 test and |  |  |  |  |  |  |  |
| after figure 2 test to check the welds and. |  |  |  |  |  |  |  |

locate any cracks.

Fig. 1-6: Standard for Floating Head Exchangers (Continued)

| In all cases: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Tests made : Figs. 1,3,4 (in the case of welded |  |  |  |  |  |  |
| tubes, test 2 shall also be made). |  |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |  |
| Fig. 1 - Intratubular space |  |  |  |  |  |  |
| a. |  |  | Tube to tube-sheet joints |  |  |  |
| b. |  |  | Tube failure |  |  |  |
| c. |  |  | Floating head and gasket |  |  |  |
| Fig 2 - Extra tubular space |  |  |  |  |  |  |
| a. |  |  | Tube to tube-sheet joints |  |  |  |
| b. |  |  | Tube failure |  |  |  |
| Fig 3 - Testing of shell |  |  |  |  |  |  |
| d. |  | Shell |  |  |  |  |
| e. |  | Gasket between shell and tube-sheet |  |  |  |  |
| Fig 4- Testing of channel |  |  |  |  |  |  |
| f. | Testing of channel |  |  |  |  |  |
| g. | Gasket between channel and tube-sheet |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |
| (1) For tubes welded to the tube-sheet, a |  |  |  |  |  |  |
| dye-penetrant examination or test with |  |  |  |  |  |  |
| ammonia must be conducted before |  |  |  |  |  |  |
| figure 1 test and after figure 2 test to |  |  |  |  |  |  |
| check the welds and locate any cracks. |  |  |  |  |  |  |

Fig. 2-1: Standard for U-Tube Exchangers

Tests made : Fig. 1,2 (Note 2),3,4. Elements tested:. Fig. 1 - Intratubular space. a.; Tube to tube-sheet joints. b.; Tube failure. Fig 2 - Extra tubular space. g.; Shell. h.; Test of Gasket between shell and tube-sheet. j.; Tube to tube-sheet joints. k.; Tube failure. Fig 3 - Test of channel. c.; Test of channel. d.; Test of gasket between channel and channel. cover and tube-sheet. Fig 4- Test of shell. f.; Test of Gasket between shell and tube-sheet. g.; Test of shell. Case 2- bundle pressure > shell pressure. Test made: Figs. 2,3. Elements tested:. Fig. 2 - See Case 1. Fig. 3 - See Case 1. Notes:. (1) For tubes welded to the tube-sheet, a dye-. penetrant examination or test with ammonia must. be conducted before and after figures 1 or 2 tests to. check and to locate any cracks.. (2) This test is made only when the tubes are welded. to the tube-sheet..

Fig. 2-2: Standard for U-Tube Exchangers (Continued)

| Case 1- Shell pressure ≥ bundle pressure |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Tests made : Figs. 2,3,4 |  |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |  |
| Fig. 2 - Extra tubular space |  |  |  |  |  |  |
| a. | Tube to tube-sheet joints |  |  |  |  |  |
| b. | Tube failure |  |  |  |  |  |
| Fig 3 - Test of channel |  |  |  |  |  |  |
| c. | Channel |  |  |  |  |  |
| d. | Test of gasket between channel and tube-sheet |  |  |  |  |  |
| Fig 4 - Test of shell |  |  |  |  |  |  |
| e. | Test of shell |  |  |  |  |  |
| f. | Test of gasket between shell and tube-sheet |  |  |  |  |  |
| Case 2- Bundle pressure > shell pressure |  |  |  |  |  |  |
| Test made: Figs. 1,2 (Note 2),3,4 |  |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |  |
| Fig. 1 - Intratubular space |  |  |  |  |  |  |
| a. |  | Tube to tube-sheet joints |  |  |  |  |
| b. |  | Tube failure |  |  |  |  |
| Fig. 2 - See Case 1 |  |  |  |  |  |  |
| Fig. 3 - See Case 1 |  |  |  |  |  |  |
| Fig. 4 - See Case 1 |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |
| (1) For tubes welded to the tube-sheet, a dye- |  |  |  |  |  |  |
| Penetrant examination or test with ammonia must |  |  |  |  |  |  |
| be conducted before and after the hydraulic test to |  |  |  |  |  |  |
| locate any cracking. |  |  |  |  |  |  |
| (2) This test is made only when the tubes are welded |  |  |  |  |  |  |
| to the tube-sheet. |  |  |  |  |  |  |

Fig. 2-3: Standard for U-Tube Exchangers (Continued)

| Case1-Shell pressure ≥ bundle pressure |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Tests made : Figs. 2,3 |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |
| Fig. 2 - Extra tubular space |  |  |  |  |  |
| a. |  | Tube to tube-sheet joints |  |  |  |
| b. |  | Tube failure |  |  |  |
| c. |  | Gasket between shell and channel |  |  |  |
| d. |  | Shell |  |  |  |
| Fig 3 - Intratubular space |  |  |  |  |  |
| e. |  | Tube to tube-sheet joints |  |  |  |
| f. |  | Gasket between channel and |  |  |  |
|  |  | channel cover |  |  |  |
| Case2-Bundle pressure > shell pressure |  |  |  |  |  |
| Tests made : Figs. 1,2 |  |  |  |  |  |
| Fig. 1 - Intratubular space |  |  |  |  |  |
| a. | Tube to tube-sheet joints |  |  |  |  |
| b. | Tube failure |  |  |  |  |
| c. | Channel |  |  |  |  |
| d. | Gasket between channel and |  |  |  |  |
|  | channel cover |  |  |  |  |
| Fig 2 - Extra tubular space |  |  |  |  |  |
| c. | Gasket between shell and channel |  |  |  |  |
| d. | Shell |  |  |  |  |
| Notes: |  |  |  |  |  |
| (1) For tubes welded to the tube-sheet, a |  |  |  |  |  |
| dye-penetrant examination or test with |  |  |  |  |  |
| ammonia must be conducted before |  |  |  |  |  |
| figure 1 test and after figure 2 test to |  |  |  |  |  |
| check the welds and locate any cracks. |  |  |  |  |  |

Fig. 2-4: Standard for U-Tube Exchangers (Continued)

| Case 1- Shell pressure ≥ bundle pressure |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Tests made : Figs. 2,3,4 |  |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |  |
| Fig. 2 - Extra tubular space |  |  |  |  |  |  |
| a. |  | Tube to tube-sheet joints |  |  |  |  |
| b. |  | Tube failure |  |  |  |  |
| Fig 3 - Test of channel |  |  |  |  |  |  |
| c. | Channel |  |  |  |  |  |
| d. | Test of gasket between channel and tube-sheet |  |  |  |  |  |
| Fig 4 - Test of shell |  |  |  |  |  |  |
| e. | Test of shell |  |  |  |  |  |
| f. | Test of gasket between shell and tube-sheet |  |  |  |  |  |
| Case 2- Bundle pressure > shell pressure |  |  |  |  |  |  |
| Test made: Figs. 1,2 (Note 2),3,4 |  |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |  |
| Fig. 1 - Intratubular space |  |  |  |  |  |  |
| a. |  | Tube to tube-sheet joints |  |  |  |  |
| b. |  | Tube failure |  |  |  |  |
| Fig. 2 - See Case 1 |  |  |  |  |  |  |
| Fig. 3 - See Case 1 |  |  |  |  |  |  |
| Fig. 4 - See Case 1 |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |
| (1) For tubes welded to the tube-sheet, a dye-penetrant |  |  |  |  |  |  |
| examination or test with ammonia must be |  |  |  |  |  |  |
| conducted before and after figure 2 tests to check |  |  |  |  |  |  |
| the welds and locate any cracks. |  |  |  |  |  |  |
| (2) This test is made only when the tubes are welded |  |  |  |  |  |  |
| to the tube-sheet. |  |  |  |  |  |  |

Fig. 2-5: Standard for U-Tube Exchangers (Continued)

| Case1-Shell pressure ≥ bundle pressure |  |  |  |  |
| --- | --- | --- | --- | --- |
| Tests made : Figs. 1,2,3 |  |  |  |  |
| Elements tested: |  |  |  |  |
| Fig. 1 - Intratubular space |  |  |  |  |
| a. | Tube to tube-sheet joints |  |  |  |
| b. | Tube failure |  |  |  |
| Fig 2 - Extra tubular space |  |  |  |  |
| a. | Tube to tube-sheet joints |  |  |  |
| b. | Tube failure |  |  |  |
| c. | Test of shell |  |  |  |
| d. | Test of gasket between shell and tube-sheet |  |  |  |
| Fig. 3 - Test of channel |  |  |  |  |
| e. | Test of channel |  |  |  |
| f. | Test of gasket between channel and stationary |  |  |  |
| tube-sheet, and between channel and channel cover |  |  |  |  |
| Case2-Bundle pressure > shell pressure |  |  |  |  |
| Tests made : Figs. 2,3 |  |  |  |  |
| Elements tested: |  |  |  |  |
| Fig. 2 - See Case 1 |  |  |  |  |
| Fig. 3 - See Case 1 |  |  |  |  |
| Notes: |  |  |  |  |
| (1) For tubes welded to the tube-sheet, a |  |  |  |  |
| dye-penetrant examination or test with |  |  |  |  |
| ammonia must be conducted before |  |  |  |  |
| figure 1 test and after figure 2 test to |  |  |  |  |
| check the welds and locate any cracks. |  |  |  |  |

Fig. 3-1: Standard for Fixed Tube sheets Exchangers

| Case1-Shell pressure ≥ bundle pressure |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Tests made : Figs. 1,2 |  |  |  |  |  |
| Elements tested: |  |  |  |  |  |
| Fig. 1 - Extra tubular space |  |  |  |  |  |
| a. | Shell |  |  |  |  |
| b. | Tube to tube-sheet joints |  |  |  |  |
| c. | Tube failure |  |  |  |  |
| Fig 2 -Intratubular space |  |  |  |  |  |
| d. | Stationary head-bonnet |  |  |  |  |
| e. | Gasket between bonnet and shell |  |  |  |  |
| f. | Gasket between shell and channel |  |  |  |  |
| g. | Channel |  |  |  |  |
| h. | Gasket between channel and channel cover |  |  |  |  |
| Case2-Bundle pressure > shell pressure |  |  |  |  |  |
| Same tests as Case 1, but for figure 2 tests: |  |  |  |  |  |
| - Do not drain after the test of the shell (figure 1 tests) |  |  |  |  |  |
| - Fit a glass tube onto an obturator in an upper nozzle |  |  |  |  |  |
| of the shell. |  |  |  |  |  |
| - Continue filling the shell until the water appears in |  |  |  |  |  |
| the glass tube. |  |  |  |  |  |
| - Pressurize the channel and channel cover and note |  |  |  |  |  |
| the water level in the glass tube. |  |  |  |  |  |
| Any leaks at the tube to tube-sheet joints will be |  |  |  |  |  |
| indicated by the change of level in the glass tube. |  |  |  |  |  |
| Notes: |  |  |  |  |  |
| (1) For tubes welded to the tube-sheet, a dye-penetrant |  |  |  |  |  |
| examination or test with ammonia must be |  |  |  |  |  |
| conducted before and after the hydraulic test to |  |  |  |  |  |
| locate any cracking. |  |  |  |  |  |

Fig. 3-2: Standard for Fixed Tube sheets Exchangers (Continued)

| Case1-Shell pressure ≥ bundle pressure |  |  |  |
| --- | --- | --- | --- |
| Tests made : Figs. 1,2 |  |  |  |
| Elements tested: |  |  |  |
| Fig. 1 - Extra tubular space |  |  |  |
| a. | Shell |  |  |
| b. | Tube to tube-sheet joints |  |  |
| c. | Tube failure |  |  |
| Fig 2 -Intratubular space |  |  |  |
| d. | Bonnet |  |  |
| e. | Gasket between bonnet and |  |  |
|  | bonnet cover |  |  |
| g. | Channel |  |  |
| h. | Gasket between channel and |  |  |
|  | channel cover |  |  |
| Case2-Bundle pressure > shell pressure |  |  |  |
| Same tests as Case 1, but for figure 2 tests: |  |  |  |
| - Do not drain after the test of the shell |  |  |  |
| (figure 1 tests) |  |  |  |
| - Fit a glass tube onto an obturator in an |  |  |  |
| upper nozzle of the shell. |  |  |  |
| - Continue filling the shell until the water |  |  |  |
| appears in the glass tube. |  |  |  |
| - Pressurize the channel and channel cover |  |  |  |
| and note the water level in the glass tube. |  |  |  |
| Any leaks at the tube to tube-sheet joints |  |  |  |
| will be indicated by the change of level in |  |  |  |
| the glass tube. |  |  |  |
| Notes: - For tubes welded to the tube-sheet, |  |  |  |
| a dye-penetrant examination or test with |  |  |  |
| ammonia must be conducted before and |  |  |  |
| after the hydraulic test to locate any cracking. |  |  |  |