STYRENE PARK OFFSITE Document Title: Steel Structure Calculation NATIVE FILE ATTACHED

| R1 | 22-07-2024 | IFA | J.morsali | J.Beigloo | A.Gholizadeh |
| --- | --- | --- | --- | --- | --- |
| R0 | 01-07-2024 | IFA | J.morsali | J.Beigloo | A.Gholizadeh |
| Rev. | Issued Date | DESCRIPTION | PREPARED | CHECKED | APPROVED |

REVISION RECORD SHEET

| Page | Revisions |  |  |  |  |  |  |  | Page | Revisions |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |  |  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |
| 1 | X | X |  |  |  |  |  |  | 41 |  |  |  |  |  |  |  |
| 2 | X |  |  |  |  |  |  |  | 42 |  |  |  |  |  |  |  |
| 3 | X |  |  |  |  |  |  |  | 43 |  |  |  |  |  |  |  |
| 4 | X |  |  |  |  |  |  |  | 44 |  |  |  |  |  |  |  |
| 5 | X |  |  |  |  |  |  |  | 45 |  |  |  |  |  |  |  |
| 6 | X |  |  |  |  |  |  |  | 46 |  |  |  |  |  |  |  |
| 7 | X |  |  |  |  |  |  |  | 47 |  |  |  |  |  |  |  |
| 8 | X |  |  |  |  |  |  |  | 48 |  |  |  |  |  |  |  |
| 9 | X |  |  |  |  |  |  |  | 49 |  |  |  |  |  |  |  |
| 10 | X |  |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  |
| 11 | X |  |  |  |  |  |  |  | 51 |  |  |  |  |  |  |  |
| 12 | X | X |  |  |  |  |  |  | 52 |  |  |  |  |  |  |  |
| 13 | X |  |  |  |  |  |  |  | 53 |  |  |  |  |  |  |  |
| 14 | X |  |  |  |  |  |  |  | 54 |  |  |  |  |  |  |  |
| 15 | X |  |  |  |  |  |  |  | 55 |  |  |  |  |  |  |  |
| 16 | X |  |  |  |  |  |  |  | 56 |  |  |  |  |  |  |  |
| 17 | X |  |  |  |  |  |  |  | 57 |  |  |  |  |  |  |  |
| 18 | X |  |  |  |  |  |  |  | 58 |  |  |  |  |  |  |  |
| 19 | X |  |  |  |  |  |  |  | 59 |  |  |  |  |  |  |  |
| 20 | X |  |  |  |  |  |  |  | 60 |  |  |  |  |  |  |  |
| 21 | X |  |  |  |  |  |  |  | 61 |  |  |  |  |  |  |  |
| 22 | X |  |  |  |  |  |  |  | 62 |  |  |  |  |  |  |  |
| 23 | X |  |  |  |  |  |  |  | 63 |  |  |  |  |  |  |  |
| 24 | X |  |  |  |  |  |  |  | 64 |  |  |  |  |  |  |  |
| 25 | X |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  |
| 26 | X |  |  |  |  |  |  |  | 66 |  |  |  |  |  |  |  |
| 27 | X |  |  |  |  |  |  |  | 67 |  |  |  |  |  |  |  |
| 28 | X |  |  |  |  |  |  |  | 68 |  |  |  |  |  |  |  |
| 29 | X |  |  |  |  |  |  |  | 69 |  |  |  |  |  |  |  |
| 30 | X |  |  |  |  |  |  |  | 70 |  |  |  |  |  |  |  |
| 31 | X |  |  |  |  |  |  |  | 71 |  |  |  |  |  |  |  |
| 32 | X |  |  |  |  |  |  |  | 72 |  |  |  |  |  |  |  |
| 33 | X |  |  |  |  |  |  |  | 73 |  |  |  |  |  |  |  |
| 34 | X |  |  |  |  |  |  |  | 74 |  |  |  |  |  |  |  |
| 35 | X |  |  |  |  |  |  |  | 75 |  |  |  |  |  |  |  |
| 36 | X | X |  |  |  |  |  |  | 76 |  |  |  |  |  |  |  |
| 37 | X | X |  |  |  |  |  |  | 77 |  |  |  |  |  |  |  |
| 38 | X |  |  |  |  |  |  |  | 78 |  |  |  |  |  |  |  |
| 39 | X |  |  |  |  |  |  |  | 79 |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |  | 80 |  |  |  |  |  |  |  |

TABLE OF CONTENTS

Table of Content:

1. SCOPE	4

2. CODE AND STANDARDS	4

3. REFERENCE DRAWING AND GENERAL DOCUMENT	4

4. MATERIAL	4

5. AIR COLLER TYPE	4

5.1. Weight Data	5

6. EXTERNAL LOADS	5

6.1. LOAD CASE DEFINITION	5

6.2. DEAD LOAD	6

6.2.1. Bundle dry reaction according to table 1:	6

6.2.2. weight of Attachment in FORCED Draft according to table 1:	7

6.2.3. Bundle Reaction Due to Fluid (WATER) Weight according to table 1:	7

6.2.4. Nozzle Load acc. to API 661 (1×4”)	8

6.2.5. Dead Load of Handrail & Grating	9

6.3. LIVE LOAD	10

6.4. SNOW LOAD	11

6.5. SEISMIC LOAD	12

6.6. WIND LOAD	12

7. BASE PLATE & ANCHOR BOLT DESIGN	13

8. DESIGN & ANALSIS	23

9. COMBINATION	31

10. JOINT REACTION	36

11. Steel Design	37

12. Story Drift & Deflection Control	40

- SCOPE

This calculation book covers a structural design for AIR COOLERS FOR Asalouyeh Project (ITEM: 1158). 3Dimensional model analyzed by mean of SAP 2000 (version 20.2.0.). This report contains computerized model, load evaluation and design verification.

- CODE AND STANDARDS

- ASCE7-16, AISC360-16, INBC, PART 6, Standard NO 2800

- REFERENCE DRAWING AND GENERAL DOCUMENT

- Air Cooler General Arrangement  : EI027-DMF-VD-ME-DWG-003

- MATERIAL

- Structural Steel: ST37 with Fy = 2400 kgf/cm2, Fu = 3700 kg/cm2

- Setting Bolts: A325 with Fu = 8000 kgf/cm2

- AIR COLLER TYPE

- Descriptions of Supported Equipment → Draft: FORCED

Table 1. Weight of  equipments  For 1 Units ( Total Units = 2)

|  | Total No in one Unit | Total Weight in one Unit (tonf) | Total No. for One Bay | Weight for One Bay (kgf) |
| --- | --- | --- | --- | --- |
| Bundle Frame | 1 | 0.865 | 1 | 865 |
| Tube Bundle & Headers | 1 | 2.635 | 1 | 2635 |
| sum |  |  |  | 3500 |
| Water in Tubes & Headers | 1 | 0.48 | 1 | 480 |
| sum |  |  |  | 480 |
| Plenum | 2 | 0.245 | 2 | 490 |
| Fan Ring | 2 | 0.13 | 2 | 260 |
| Motor | 2 | 0.07 | 2 | 140 |
| Fan | 2 | 0.0275 | 2 | 55 |
| Speed Reducer | 2 | 0.25 | 2 | 500 |
| Machinery Mount | 2 | 0.32 | 2 | 640 |
| Fan Guard | 2 | 0.0325 | 2 | 65 |
| sum |  |  |  | 2150 |

# 6 .EXTERNAL LOADS

# 6.1. LOAD CASE DEFINITION:

DEAD: Dead load contain weight of component (bundle dry, plenum, fan ring, fan, fan guard, motor, Speed Reducer and Machinery Mount,), dead load of walkway

DEAD-OP: weight of liquid (water) within each tube bundle

DEADS: self-weight of steel structure

DEADN: nozzle load (3 times of API)

LIVE: live load of walkway.

EQX: effect of earth quake at x- direction.

EQY: effect of earth quake at y- direction.

EQXO: Amplified Seismic Load in X Dir. (2EQX )

EQYO: Amplified Seismic Load in Y Dir. (2 EQY)

WX: effect of wind load at x- direction.

WY: effect of wind load at y- direction.

SNOW: Snow Load

6.2. DEAD LOAD

There are one bundle per each bay

6.2.1. Bundle dry according to table 1 & table 1: (figure.1)

Tube bundle , Headers and bundle frame Weight per Item (Dry): 3.5 ton

Tube bundle , Headers and bundle frame Weight of Each Bundle (Dry): 3500 kg → Wd = 3500÷(8)=437.5 kg

→ Wd = = 437.5 kg , (Point  load on transvers beams)

Figure.1

6.2.2. Weight of Attachment in FORCED Draft according to table 1: (figure.1)

TOTAL Wequipment  for Item = 2150 kg (for 1 Bay)

Wequipment =1075 kg (for One Unit)

L=5.7 m, W=2.8  m→L+2W=11.3 m

Distribution Load : Wequipment =1075/11.3= 95 kg/m

6.2.3. Bundle Reaction Due to Fluid (WATER) Weight according to table 1: (figure.2)

Weight per one unit Item (Operation: Only fluid Weight): 0.48 ton

Weight of each bundle (Operation: Only fluid Weight): 480 kg → Wo = 480÷8=60 kg →  Wo = ~60 kg (Point  load on transvers beams)

Figure.2

6.2.4. Nozzle Load Acc. to API 661:(figure .3)

Table 2. Nozzle Load for Size 4”

| Nozzle Direction | Structure Direction | API Load (kgf) |  | 3×API | Nozzlele QTY. | Final Load |
| --- | --- | --- | --- | --- | --- | --- |
| x | x | Fx = | 334 | 1002 | 1 | 1002 |
| y | z | Fy = | 267 | 801 | 1 | 801 |
| z | y | Fz = | 334 | 1002 | 1 | 1002 |

Figure.3

6.2.5. Dead Load of Handrail & Grating: (figure.4)

Weight of Grating = 45 kg/m2

Walkway Frame = 40 kg/m2

Handrail = 15 kg/m2

Width of Walkway = 0.8 m

Dead load for Walkway Beams = (45+40+15) × (0.75÷2) = 37.5 kg/m → USE: 40 kg/m

Figure.4

6.3. LIVE LOAD (figure.5)

Live Load According to API 661: 250 kg/m2

Live Load for Walkway Beams (Bearing width = 0.75÷2=0.375 m): 100 kg/m → USE: 100kg/m

Figure.5

6.4. SNOW LOAD (Figure.6)

According to INBC Part 6:

Ground Snow Loads, Ps = 50 kg/m2

Importance factor, Is = 1.2

Exposure factor, Cn = 1.1

Thermal factor, Ch = 1.0

Slope factor, Cs = 1.0

Pr = Is Cn Ch CS Pg  → Pr =1.2×1.1×1.0×1.0×50 = 66 kg/m2

Effective Area: 2.497×(6.33) = 15.81 m2

Fsnow = 66×15.81   → Fsnow = 1044 kg → Ws = 1044÷(8) → Ws = 131 kg (Point Load on Transverse beams)

Snow load for Walk Way Beams = 66×0..375 = 25 kg/m

Figure.6

## 6.5. SEISMIC LOAD

Air cooler support (steel structure) designed in accordance with Standard Standard NO 2800:

According to Standard NO 2800 : Soil Type = IV & A=0.3, I=1.4 , R=3.5

According to Standard No 2800:

T=0.08H0.75 =0.27s

T0= 0.15 ,  Ts=1 → B=2.75

C=ABIRW=0.33W

W= tube bundles (full of water)+ weight of all equipment (plenums+ fan guards+ fan Rings+ fans+ motor+ speed reducers) + self-weight of structure + nozzle load+ 0.2(access platform load+ Snow) = 12078.6 kg

Seismic base shear:

→For Ordinary braced frame V = 0.33 *12.0786= 3.9859ton

For Ordinary braced frame:

Table 6. Mass Source for one Unit (Total Units=2)

| Output Case | Global FZ (Tonf) | Multiplier | Mass Source |
| --- | --- | --- | --- |
| DEAD | 6.095 | 1 | 6.095 |
| DEAD-OP | 0.48 | 1 | 0.48 |
| DEAD-S | 3.412 | 1 | 3.412 |
| DEAD-N | 1.602 | 1 | 1.602 |
| LIVE | 1.12 | 0.2 | 0.224 |
| SNOW | 1.328 | 0.2 | 0.2656 |
| Sum |  |  | 12.0786 |

6.6. WIND LOAD

Auto WIND used for Columns, Bracing and Walkway   According to ASCE 7-16

Acc.to Client Spec, Basic wind velocity = 125 Km/hr & Exposure Category: C

# 7.7 BASE PLATE & ANCHOR BOLT DESIGN

Design

| Name | Base Plate Connection |
| --- | --- |
| Description |  |
| Analysis | Stress, strain/ simplified loading |
| Design code | AISC - LRFD (2022) |

Members

Geometry

| Name | Cross-section | β – Direction [°] | γ - Pitch [°] | α - Rotation [°] | Offset ex [mm] | Offset ey [mm] | Offset ez [mm] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| COL | 1 - CON1(HEA160) | 0.0 | 90.0 | 0.0 | 0 | 0 | 0 |

Supports and forces

| Name | Support | Forces in | X [mm] |
| --- | --- | --- | --- |
| COL / end |  | Node | 0 |

Cross-sections

| Name | Material |
| --- | --- |
| 1 - CON1(HEA160) | A36 |

Anchors

| Name | Diameter [mm] | fy [MPa] | fu [MPa] | Gross area [mm2] |
| --- | --- | --- | --- | --- |
| 24 A325M | 24 | 660.0 | 830.0 | 452 |

Load effects (Equilibrium not required)

| Name | Member | N [kN] | Vy [kN] | Vz [kN] | Mx [kNm] | My [kNm] | Mz [kNm] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LE1 | COL / End | -127.0 | 34.0 | 47.0 | 0.0 | 0.0 | 0.0 |

Foundation block

| Item | Value | Unit |
| --- | --- | --- |
| CB 1 |  |  |
| Dimensions | 950 x 950 | mm |
| Depth | 600 | mm |
| Anchor | 24 A325M |  |
| Anchoring length | 400 | mm |
| Shear force transfer | Anchors |  |

Check

Summary

| Name | Value | Check status |
| --- | --- | --- |
| Analysis | 100.0% | OK |
| Plates | 0.0 < 5.0% | OK |
| Anchors | 70.5 < 100% | OK |
| Welds | 29.8 < 100% | OK |
| Concrete block | 4.8 < 100% | OK |
| Buckling | Not calculated |  |

Plates

| Name | tp [mm] | Loads | σEd [MPa] | εPl [%] | σc,Ed [MPa] | Status |
| --- | --- | --- | --- | --- | --- | --- |
| COL-bfl 1 | 9.0 | LE1 | 164.8 | 0.0 | 0.0 | OK |
| COL-tfl 1 | 9.0 | LE1 | 97.1 | 0.0 | 0.0 | OK |
| COL-w 1 | 6.0 | LE1 | 116.6 | 0.0 | 0.0 | OK |
| BP1 | 25.0 | LE1 | 30.4 | 0.0 | 0.0 | OK |

Design data

| Material | Fy [MPa] | εlim [%] |
| --- | --- | --- |
| A36 | 248.2 | 5.0 |

Symbol explanation

| tp | Plate thickness |
| --- | --- |
| σEd | Equivalent stress |
| εPl | Plastic strain |
| σc,Ed | Contact stress |
| Fy | Yield strength |
| εlim | Limit of plastic strain |

Detailed result for COL-bfl 1

Design values used in the analysis

|  | 223.4 | MPa |
| --- | --- | --- |

Where:

|  | – characteristic yield strength |
| --- | --- |
|  | – resistance factor for steel material AISC 360-22 – B3.1 |

| Overall check, LE1 |  |  |  |
| --- | --- | --- | --- |
| Strain check, LE1 |  |  |

| Equivalent stress, LE1 |  |
| --- | --- |

| Shape | Item | Loads | Nf [kN] | V [kN] | ϕVcbg [kN] | ϕVcp [kN] | Utt [%] | Uts [%] | Utts [%] | Detailing | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A1 | LE1 | 0.0 | 14.8 | 70.9 | 444.6 | 0.0 | 70.5 | 55.8 | OK | OK |
|  | A2 | LE1 | 0.0 | 14.3 | 70.9 | 444.6 | 0.0 | 70.5 | 55.8 | OK | OK |
|  | A3 | LE1 | 0.0 | 14.3 | 77.9 | 444.6 | 0.0 | 53.1 | 34.8 | OK | OK |
|  | A4 | LE1 | 0.0 | 14.5 | - | 444.6 | 0.0 | 13.0 | 3.4 | OK | OK |

Design data

| Grade | ϕNsa [kN] | ϕVsa [kN] |
| --- | --- | --- |
| 24 A325M - 1 | 205.1 | 114.3 |

Symbol explanation

| Nf | Tension force |
| --- | --- |
| V | Resultant of bolt shear forces Vy and Vz in shear planes |
| ϕVcbg | Concrete breakout strength in shear – ACI 318-14 – 17.5.2 |
| ϕVcp | Concrete pryout strength in shear – ACI 318-14 – 17.5.3 |
| Utt | Utilization in tension |
| Uts | Utilization in shear |
| Utts | Utilization in tension and shear |
| ϕNsa | Steel strength of anchor in tension - ACI 318-14 – 17.4.1 |
| ϕVsa | Steel strength of anchor in shear - ACI 318-14 – 17.5.1 |

Detailed result for A1

Anchor tensile resistance (ACI 318-14 – 17.4.1)

|  | 205.1 | kN | ≥ |  | 0.0 | kN |
| --- | --- | --- | --- | --- | --- | --- |

Where:

|  | – resistance factor |
| --- | --- |
|  | – tensile stress area |
|  | – specified tensile strength of anchor steel: , where: 660.0 MPa – specified yield strength of anchor steel 830.0 MPa – specified ultimate strength of anchor steel |

Shear resistance (ACI 318-14 – 17.5.1)

|  | 114.3 | kN | ≥ |  | 14.8 | kN |
| --- | --- | --- | --- | --- | --- | --- |

Where:

|  | – resistance factor |
| --- | --- |
|  | – tensile stress area |
|  | – specified tensile strength of anchor steel: |
| , where: 660.0 MPa – specified yield strength of anchor steel 830.0 MPa – specified ultimate strength of anchor steel |  |

Concrete shear breakout check (ACI 318-14 – 17.5.2)
The check is performed for group of anchors that form common shear breakout cone: A1, A2

|  | 70.9 | kN | ≥ |  | 50.0 | kN |
| --- | --- | --- | --- | --- | --- | --- |

Where:

|  | – sum of shear forces of anchors on common base plate |
| --- | --- |
|  | – resistance factor |
|  | – projected concrete failure area of an anchor or group of anchors |
|  | – projected concrete failure area of one anchor when not limited by corner influences, spacing or member thickness |
|  | – modification factor for anchor groups loaded eccentrically in shear: |
| , where: 0 mm – shear load eccentricity 354 mm – edge distance in direction of the load 354 mm – edge distance in direction of the load |  |
|  | – modification factor for edge effect: |
| , where: 354 mm – edge distance in direction of the load 354 mm – edge distance in direction of the load 355 mm – edge distance in direction perpendicular to the load |  |
|  | – modification factor for concrete conditions |
|  | – modification factor for anchors located in a shallow concrete member: |
| , where: 600 mm – thickness of member in which an anchor is anchored measured parallel to anchor axis |  |
|  | – modification factor for anchors loaded at an angle with the concrete edge |
| , where: 19.9 ° – angle between direction of shear force and direction perpendicular to concrete edge |  |
|  | – basic concrete breakout strength of a single anchor in shear: |
| , where: 192 mm – effective length 24 mm – anchor diameter 1.00 – modification factor for lightweight concrete 27.6 MPa – concrete compressive strength 354 mm – edge distance in direction of the load 354 mm – edge distance in direction of the load |  |

Concrete pryout resistance (ACI 318-14 – 17.5.3)
The check is performed for group of anchors on common base plate

|  | 444.6 | kN | ≥ |  | 58.0 | kN |
| --- | --- | --- | --- | --- | --- | --- |

Where:

|  | – resistance factor |
| --- | --- |
|  | – concrete pry-out factor |
|  | – concrete cone tension break-out resistance in case all anchors are in tension |
|  | – sum of shear forces of anchors on common base plate |

Interaction of tensile and shear forces (ACI 318-14 – R17.6)

|  | 0.56 | ≤ | 1.0 |
| --- | --- | --- | --- |

Where:

|  | – maximum ratio of factored tensile force and tensile resistance determined from all appropriate failure modes |
| --- | --- |
|  | – maximum ratio of factored shear force and shear resistance determined from all appropriate failure modes |

Welds

| Item | Edge | Xu | tw [mm] | w [mm] | L [mm] | Lc [mm] | Loads | Fn [kN] | ϕRn [kN] | Ut [%] | Detailing | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BP1 | COL-bfl 1 | E70xx | ◢ 4.9 ◣ | ◢ 7.0 ◣ | 159 | 13 | LE1 | 6.0 | 20.1 | 29.8 | OK | OK |
|  |  | E70xx | ◢ 4.9 ◣ | ◢ 7.0 ◣ | 159 | 13 | LE1 | 5.4 | 20.2 | 26.9 | OK | OK |
| BP1 | COL-tfl 1 | E70xx | ◢ 4.9 ◣ | ◢ 7.0 ◣ | 159 | 13 | LE1 | 4.7 | 19.8 | 23.6 | OK | OK |
|  |  | E70xx | ◢ 4.9 ◣ | ◢ 7.0 ◣ | 159 | 13 | LE1 | 4.1 | 19.4 | 21.2 | OK | OK |
| BP1 | COL-w 1 | E70xx | ◢ 4.9 ◣ | ◢ 7.0 ◣ | 142 | 13 | LE1 | 2.5 | 15.6 | 15.7 | OK | OK |
|  |  | E70xx | ◢ 4.9 ◣ | ◢ 7.0 ◣ | 142 | 13 | LE1 | 2.4 | 15.1 | 15.8 | OK | OK |

Design data

| Material | Fexx [MPa] |
| --- | --- |
| E70xx | 482.6 |

Symbol explanation

| tw | Throat thickness of weld |
| --- | --- |
| w | Leg size of weld |
| L | Length of weld |
| Lc | Length of weld critical element |
| Fn | Force in weld critical element |
| ϕRn | Weld resistance - AISC 360-22 – J2-4 |
| Ut | Utilization |
| ◢ | Fillet weld |
| Fexx | Ultimate strength as rated by electrode classification number |

Detailed result for BP1 / COL-bfl 1

Weld resistance check (AISC 360-22 – J2-4)

|  | 20.1 | kN | ≥ |  | 6.0 | kN |
| --- | --- | --- | --- | --- | --- | --- |

Where:

|  | – nominal stress of weld material: |
| --- | --- |
| , where: 482.6 MPa – electrode classification number, i.e. minimum specified tensile strength 60.3° – angle of loading measured from the weld longitudinal axis |  |
|  | – effective area of weld critical element |
|  | – resistance factor for welded connections |

| Item | Loads | A1 [mm2] | A2 [mm2] | σ [MPa] | ϕfp,max [MPa] | Ut [%] | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CB 1 | LE1 | 86506 | 705173 | 1.5 | 30.5 | 4.8 | OK |

Symbol explanation

| A1 | Loaded area |
| --- | --- |
| A2 | Supporting area |
| σ | Average stress in concrete |
| ϕfp,max | Concrete bearing resistance |
| Ut | Utilization |

Detailed result for CB 1

Concrete block compressive resistance check (AISC 360-22 – J8)

|  | 30.5 | MPa | ≥ |  | 1.5 | MPa |
| --- | --- | --- | --- | --- | --- | --- |

Where:

|  | – concrete block design bearing strength: |
| --- | --- |
| , where: 27.6 MPa – concrete compressive strength 86506 mm2 – base plate area in contact with concrete surface 705173 mm2 – concrete supporting surface |  |
|  | – resistance factor for concrete |

# 8.   DESIGN & ANALYSIS

9.  COMBINATION

Table:  Combination Definitions, Part 1 of 3

| Table: Combination Definitions, Part 1 of 3 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ComboName | ComboType | AutoDesign | CaseType | CaseName | ScaleFactor | SteelDesign |
| COMB01 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.4 | Strength |
| COMB02 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB02 |  |  | Linear Static | LIVE | 1.6 |  |
| COMB02 |  |  | Linear Static | SNOW | 0.5 |  |
| COMB03 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB03 |  |  | Linear Static | SNOW | 1.6 |  |
| COMB03 |  |  | Linear Static | LIVE | 1 |  |
| COMB04 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB04 |  |  | Linear Static | SNOW | 1.6 |  |
| COMB04 |  |  | Linear Static | WX | 0.7 |  |
| COMB05 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB05 |  |  | Linear Static | SNOW | 1.6 |  |
| COMB05 |  |  | Linear Static | WX | -0.7 |  |
| COMB06 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB06 |  |  | Linear Static | SNOW | 1.6 |  |
| COMB06 |  |  | Linear Static | WY | 0.7 |  |
| COMB07 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB07 |  |  | Linear Static | SNOW | 1.6 |  |
| COMB07 |  |  | Linear Static | WY | -0.7 |  |
| COMB08 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB08 |  |  | Linear Static | WX | 1.4 |  |
| COMB08 |  |  | Linear Static | LIVE | 1 |  |
| COMB08 |  |  | Linear Static | SNOW | 0.5 |  |
| COMB09 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB09 |  |  | Linear Static | WX | -1.4 |  |
| COMB09 |  |  | Linear Static | LIVE | 1 |  |
| COMB09 |  |  | Linear Static | SNOW | 0.5 |  |
| COMB10 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB10 |  |  | Linear Static | WY | 1.4 |  |
| COMB10 |  |  | Linear Static | LIVE | 1 |  |
| COMB10 |  |  | Linear Static | SNOW | 0.5 |  |
| COMB11 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |
| COMB11 |  |  | Linear Static | WY | -1.4 |  |
| COMB11 |  |  | Linear Static | LIVE | 1 |  |
| COMB11 |  |  | Linear Static | SNOW | 0.5 |  |
| COMB12 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.9 | Strength |
| COMB12 |  |  | Linear Static | WX | 1.4 |  |
| COMB13 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.9 | Strength |
| COMB13 |  |  | Linear Static | WX | -1.4 |  |
| COMB14 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.9 | Strength |
| COMB14 |  |  | Linear Static | WY | 1.4 |  |
| COMB15 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.9 | Strength |
| COMB15 |  |  | Linear Static | WY | -1.4 |  |
| E_COMB01 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB01 |  |  | Linear Static | EQX | 1 |  |
| E_COMB01 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB01 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB02 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB02 |  |  | Linear Static | EQX | -1 |  |
| E_COMB02 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB02 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB03 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB03 |  |  | Linear Static | EQY | 1 |  |
| E_COMB03 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB03 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB04 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB04 |  |  | Linear Static | EQY | -1 |  |
| E_COMB04 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB04 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB05 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB05 |  |  | Linear Static | EQX | 1 |  |
| E_COMB06 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB06 |  |  | Linear Static | EQX | -1 |  |
| E_COMB07 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB07 |  |  | Linear Static | EQY | 1 |  |
| E_COMB08 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB08 |  |  | Linear Static | EQY | -1 |  |
| E_COMB09 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB09 |  |  | Linear Static | EQX | 1 |  |
| E_COMB09 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB09 |  |  | Linear Static | EQY | 0.3 |  |
| E_COMB09 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB10 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB10 |  |  | Linear Static | EQX | 1 |  |
| E_COMB10 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB10 |  |  | Linear Static | EQY | -0.3 |  |
| E_COMB10 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB11 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB11 |  |  | Linear Static | EQX | -1 |  |
| E_COMB11 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB11 |  |  | Linear Static | EQY | -0.3 |  |
| E_COMB11 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB13 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB13 |  |  | Linear Static | EQY | 1 |  |
| E_COMB13 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB13 |  |  | Linear Static | EQX | 0.3 |  |
| E_COMB13 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB14 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB14 |  |  | Linear Static | EQY | 1 |  |
| E_COMB14 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB14 |  |  | Linear Static | EQX | -0.3 |  |
| E_COMB14 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB15 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB15 |  |  | Linear Static | EQY | -1 |  |
| E_COMB15 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB15 |  |  | Linear Static | EQX | -0.3 |  |
| E_COMB15 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB16 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB16 |  |  | Linear Static | EQY | -1 |  |
| E_COMB16 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB16 |  |  | Linear Static | EQX | 0.3 |  |
| E_COMB16 |  |  | Linear Static | SNOW | 0.2 |  |
| E_COMB17 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB17 |  |  | Linear Static | EQX | 1 |  |
| E_COMB17 |  |  | Linear Static | EQY | 0.3 |  |
| E_COMB18 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB18 |  |  | Linear Static | EQX | 1 |  |
| E_COMB18 |  |  | Linear Static | EQY | -0.3 |  |
| E_COMB19 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB19 |  |  | Linear Static | EQX | -1 |  |
| E_COMB19 |  |  | Linear Static | EQY | -0.3 |  |
| E_COMB20 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB20 |  |  | Linear Static | EQX | -1 |  |
| E_COMB20 |  |  | Linear Static | EQY | 0.3 |  |
| E_COMB21 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB21 |  |  | Linear Static | EQY | 1 |  |
| E_COMB21 |  |  | Linear Static | EQX | 0.3 |  |
| E_COMB22 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB22 |  |  | Linear Static | EQY | 1 |  |
| E_COMB22 |  |  | Linear Static | EQX | -0.3 |  |
| E_COMB23 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB23 |  |  | Linear Static | EQY | -1 |  |
| E_COMB23 |  |  | Linear Static | EQX | -0.3 |  |
| E_COMB24 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| E_COMB24 |  |  | Linear Static | EQY | -1 |  |
| E_COMB24 |  |  | Linear Static | EQX | 0.3 |  |
| E_COMB12 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| E_COMB12 |  |  | Linear Static | EQX | -1 |  |
| E_COMB12 |  |  | Linear Static | LIVE | 1 |  |
| E_COMB12 |  |  | Linear Static | EQY | 0.3 |  |
| E_COMB12 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB01 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB01 |  |  | Linear Static | EQXO | 1 |  |
| ES_COMB01 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB01 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB02 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.3 | Strength |
| ES_COMB02 |  |  | Linear Static | EQXO | -1 |  |
| ES_COMB02 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB02 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB03 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB03 |  |  | Linear Static | EQYO | 1 |  |
| ES_COMB03 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB03 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB04 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB04 |  |  | Linear Static | EQYO | -1 |  |
| ES_COMB04 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB04 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB05 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB05 |  |  | Linear Static | EQXO | 1 |  |
| ES_COMB06 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB06 |  |  | Linear Static | EQXO | -1 |  |
| ES_COMB07 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB07 |  |  | Linear Static | EQYO | 1 |  |
| ES_COMB08 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB08 |  |  | Linear Static | EQYO | -1 |  |
| ES_COMB09 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB09 |  |  | Linear Static | EQXO | 1 |  |
| ES_COMB09 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB09 |  |  | Linear Static | EQYO | 0.3 |  |
| ES_COMB09 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB10 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB10 |  |  | Linear Static | EQXO | 1 |  |
| ES_COMB10 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB10 |  |  | Linear Static | EQYO | -0.3 |  |
| ES_COMB10 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB11 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB11 |  |  | Linear Static | EQXO | -1 |  |
| ES_COMB11 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB11 |  |  | Linear Static | EQYO | -0.3 |  |
| ES_COMB11 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB13 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB13 |  |  | Linear Static | EQYO | 1 |  |
| ES_COMB13 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB13 |  |  | Linear Static | EQXO | 0.3 |  |
| ES_COMB13 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB14 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB14 |  |  | Linear Static | EQYO | 1 |  |
| ES_COMB14 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB14 |  |  | Linear Static | EQXO | -0.3 |  |
| ES_COMB14 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB15 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB15 |  |  | Linear Static | EQYO | -1 |  |
| ES_COMB15 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB15 |  |  | Linear Static | EQXO | -0.3 |  |
| ES_COMB15 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB16 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB16 |  |  | Linear Static | EQYO | -1 |  |
| ES_COMB16 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB16 |  |  | Linear Static | EQXO | 0.3 |  |
| ES_COMB16 |  |  | Linear Static | SNOW | 0.2 |  |
| ES_COMB17 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB17 |  |  | Linear Static | EQXO | 1 |  |
| ES_COMB17 |  |  | Linear Static | EQYO | 0.3 |  |
| ES_COMB18 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB18 |  |  | Linear Static | EQXO | 1 |  |
| ES_COMB18 |  |  | Linear Static | EQYO | -0.3 |  |
| ES_COMB19 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB19 |  |  | Linear Static | EQXO | -1 |  |
| ES_COMB19 |  |  | Linear Static | EQYO | -0.3 |  |
| ES_COMB20 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB20 |  |  | Linear Static | EQXO | -1 |  |
| ES_COMB20 |  |  | Linear Static | EQYO | 0.3 |  |
| ES_COMB21 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB21 |  |  | Linear Static | EQYO | 1 |  |
| ES_COMB21 |  |  | Linear Static | EQXO | 0.3 |  |
| ES_COMB22 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB22 |  |  | Linear Static | EQYO | 1 |  |
| ES_COMB22 |  |  | Linear Static | EQXO | -0.3 |  |
| ES_COMB23 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB23 |  |  | Linear Static | EQYO | -1 |  |
| ES_COMB23 |  |  | Linear Static | EQXO | -0.3 |  |
| ES_COMB24 | Linear Add | No | Linear Static | DEAD_TOTAL | 0.735 | Strength |
| ES_COMB24 |  |  | Linear Static | EQYO | -1 |  |
| ES_COMB24 |  |  | Linear Static | EQXO | 0.3 |  |
| ES_COMB12 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.365 | Strength |
| ES_COMB12 |  |  | Linear Static | EQXO | -1 |  |
| ES_COMB12 |  |  | Linear Static | LIVE | 1 |  |
| ES_COMB12 |  |  | Linear Static | EQYO | 0.3 |  |
| ES_COMB12 |  |  | Linear Static | SNOW | 0.2 |  |
| DEF_COMB1 | Linear Add | No | Linear Static | DEAD_TOTAL | 1 | Strength |
| DEF_COMB2 | Linear Add | No | Linear Static | LIVE | 1 | Strength |
| DEF_COMB3 | Linear Add | No | Linear Static | DEAD_TOTAL | 1 | Strength |
| DEF_COMB3 |  |  | Linear Static | LIVE | 1 |  |
| DEF_COMB4 | Linear Add | No | Linear Static | DEAD_TOTAL | 1 | Strength |
| DEF_COMB4 |  |  | Linear Static | SNOW | 0.55 |  |
| COMB00 | Linear Add | No | Linear Static | DEAD_TOTAL | 1.2 | Strength |

10.   JOINT REACTION

Table:  Joint Reactions

| Table: Joint Reactions |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Joint | OutputCase | CaseType | F1 | F2 | F3 | M1 | M2 | M3 |
|  |  |  | Kgf | Kgf | Kgf | Kgf-cm | Kgf-cm | Kgf-cm |
| A-1 | DEAD_S | LinStatic | 16.65 | -45 | 861.98 | 0 | 0 | 0 |
| A-1 | DEAD | LinStatic | 49.34 | -158.83 | 1640.14 | 0 | 0 | 0 |
| A-1 | DEAD_OP | LinStatic | 4.08 | -14.37 | 92.37 | 0 | 0 | 0 |
| A-1 | DEAD_N | LinStatic | -1631.93 | 429.16 | -2881.5 | 0 | 0 | 0 |
| A-1 | LIVE | LinStatic | 3.34 | 25.54 | 1383.73 | 0 | 0 | 0 |
| A-1 | WX | LinStatic | 31.57 | 329.34 | -352.72 | 0 | 0 | 0 |
| A-1 | WY | LinStatic | -387.76 | 93.94 | -669.09 | 0 | 0 | 0 |
| A-1 | SNOW | LinStatic | 9.74 | -24.99 | 547.6 | 0 | 0 | 0 |
| A-1 | EQX | LinStatic | 106.43 | 1146.34 | -1764.17 | 0 | 0 | 0 |
| A-1 | EQY | LinStatic | -1561.76 | 337 | -3289.21 | 0 | 0 | 0 |
| A-1 | EQXO | LinStatic | 210.24 | 2295.43 | -3529.78 | 0 | 0 | 0 |
| A-1 | EQYO | LinStatic | -3123.79 | 673.24 | -6571.39 | 0 | 0 | 0 |
| A-2 | DEAD_S | LinStatic | -20.6 | 1.599E-13 | 380.54 | 0 | 0 | 0 |
| A-2 | DEAD | LinStatic | -33.06 | -2.89E-06 | 811.07 | 0 | 0 | 0 |
| A-2 | DEAD_OP | LinStatic | -0.21 | -3.963E-07 | 55.27 | 0 | 0 | 0 |
| A-2 | DEAD_N | LinStatic | -10.59 | -1.13 | -378.95 | 0 | 0 | 0 |
| A-2 | LIVE | LinStatic | -76.47 | 6.353E-13 | 402.18 | 0 | 0 | 0 |
| A-2 | WX | LinStatic | 1.165E-12 | 49.87 | 8.288E-13 | 0 | 0 | 0 |
| A-2 | WY | LinStatic | -54.91 | -1.269E-13 | -353.83 | 0 | 0 | 0 |
| A-2 | SNOW | LinStatic | -19.58 | -8.653E-07 | 221.21 | 0 | 0 | 0 |
| A-2 | EQX | LinStatic | 0.004107 | 45.8 | 0.09216 | 0 | 0 | 0 |
| A-2 | EQY | LinStatic | -48.82 | -0.38 | -1465.12 | 0 | 0 | 0 |
| A-2 | EQXO | LinStatic | 0.00889 | 92.7 | 0.18 | 0 | 0 | 0 |
| A-2 | EQYO | LinStatic | -98.54 | -0.78 | -2927.34 | 0 | 0 | 0 |
| A-3 | DEAD_S | LinStatic | 16.65 | 45 | 861.98 | 0 | 0 | 0 |
| A-3 | DEAD | LinStatic | 49.34 | 158.83 | 1640.17 | 0 | 0 | 0 |
| A-3 | DEAD_OP | LinStatic | 4.08 | 14.37 | 92.37 | 0 | 0 | 0 |
| A-3 | DEAD_N | LinStatic | 39.17 | 235.02 | 482.86 | 0 | 0 | 0 |
| A-3 | LIVE | LinStatic | 3.34 | -25.54 | 1383.73 | 0 | 0 | 0 |
| A-3 | WX | LinStatic | -31.57 | 329.34 | 352.72 | 0 | 0 | 0 |
| A-3 | WY | LinStatic | -387.76 | -93.94 | -669.09 | 0 | 0 | 0 |
| A-3 | SNOW | LinStatic | 9.74 | 24.99 | 547.61 | 0 | 0 | 0 |
| A-3 | EQX | LinStatic | -106.49 | 1146.49 | 1764.07 | 0 | 0 | 0 |
| A-3 | EQY | LinStatic | -1071.77 | -428.48 | -2570.23 | 0 | 0 | 0 |
| A-3 | EQXO | LinStatic | -210.36 | 2295.75 | 3529.6 | 0 | 0 | 0 |
| A-3 | EQYO | LinStatic | -2144 | -856.2 | -5134.3 | 0 | 0 | 0 |
| B-1 | DEAD_S | LinStatic | 34.11 | -1.44 | 482.68 | 0 | 0 | 0 |
| B-1 | DEAD | LinStatic | 174.23 | -2.24 | 983.92 | 0 | 0 | 0 |
| B-1 | DEAD_OP | LinStatic | 16.3 | 0.03128 | 81.45 | 0 | 0 | 0 |
| B-1 | DEAD_N | LinStatic | -670.87 | 1.33 | 2555.04 | 0 | 0 | 0 |
| B-1 | LIVE | LinStatic | -43.74 | -6.51 | 64.14 | 0 | 0 | 0 |
| B-1 | WX | LinStatic | -255.25 | 0.99 | -374.63 | 0 | 0 | 0 |
| B-1 | WY | LinStatic | -1.33 | -70.96 | 504.74 | 0 | 0 | 0 |
| B-1 | SNOW | LinStatic | 24.65 | -1.56 | 193.87 | 0 | 0 | 0 |
| B-1 | EQX | LinStatic | -985.73 | 4.1 | -1834.5 | 0 | 0 | 0 |
| B-1 | EQY | LinStatic | -51.12 | -28.6 | 2619.38 | 0 | 0 | 0 |
| B-1 | EQXO | LinStatic | -1968.03 | 8.18 | -3658.39 | 0 | 0 | 0 |
| B-1 | EQYO | LinStatic | -102.38 | -57.85 | 5233.15 | 0 | 0 | 0 |
| B-2 | DEAD_S | LinStatic | -3.76E-15 | -9.82 | 342.79 | 0 | 0 | 0 |
| B-2 | DEAD | LinStatic | -1.168E-10 | -61.15 | 847.79 | 0 | 0 | 0 |
| B-2 | DEAD_OP | LinStatic | -1.602E-11 | -8.01 | 77.09 | 0 | 0 | 0 |
| B-2 | DEAD_N | LinStatic | -0.0003857 | -403.24 | 720.08 | 0 | 0 | 0 |
| B-2 | LIVE | LinStatic | 8.844E-15 | 82.81 | -147.91 | 0 | 0 | 0 |
| B-2 | WX | LinStatic | -56.07 | 3.583E-12 | -6.399E-12 | 0 | 0 | 0 |
| B-2 | WY | LinStatic | -8.004E-14 | -439.42 | 682.53 | 0 | 0 | 0 |
| B-2 | SNOW | LinStatic | -3.498E-11 | 3.21 | 131.34 | 0 | 0 | 0 |
| B-2 | EQX | LinStatic | 0.02819 | 0.04229 | -0.07544 | 0 | 0 | 0 |
| B-2 | EQY | LinStatic | 0.006383 | -1570.51 | 2804.88 | 0 | 0 | 0 |
| B-2 | EQXO | LinStatic | -0.2 | 0.08416 | -0.15 | 0 | 0 | 0 |
| B-2 | EQYO | LinStatic | 0.0007535 | -3138.25 | 5603.81 | 0 | 0 | 0 |
| B-3 | DEAD_S | LinStatic | -34.11 | -1.44 | 482.68 | 0 | 0 | 0 |
| B-3 | DEAD | LinStatic | -174.23 | -2.24 | 983.9 | 0 | 0 | 0 |
| B-3 | DEAD_OP | LinStatic | -16.3 | 0.03128 | 81.45 | 0 | 0 | 0 |
| B-3 | DEAD_N | LinStatic | -670.07 | 1.26 | 1104.47 | 0 | 0 | 0 |
| B-3 | LIVE | LinStatic | 43.74 | -6.51 | 64.14 | 0 | 0 | 0 |
| B-3 | WX | LinStatic | -255.25 | -0.99 | 374.63 | 0 | 0 | 0 |
| B-3 | WY | LinStatic | 1.33 | -70.96 | 504.74 | 0 | 0 | 0 |
| B-3 | SNOW | LinStatic | -24.65 | -1.56 | 193.87 | 0 | 0 | 0 |
| B-3 | EQX | LinStatic | -985.8 | -4.09 | 1834.58 | 0 | 0 | 0 |
| B-3 | EQY | LinStatic | -40.75 | -28.68 | 1900.29 | 0 | 0 | 0 |
| B-3 | EQXO | LinStatic | -1968.16 | -8.15 | 3658.54 | 0 | 0 | 0 |
| B-3 | EQYO | LinStatic | -81.36 | -57.83 | 3796.07 | 0 | 0 | 0 |

11.  Steel Design

Table:  Steel Design 1 - Summary Data - AISC 360-16, Part 1 of 2

| Table: Steel Design 1 - Summary Data - AISC 360-16, Part 1 of 2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Frame | DesignSect | DesignType | Status | Ratio | RatioType |
| 99 | HE160A | Column | No Messages | 0.253046 | PMM |
| 101 | HE160A | Column | No Messages | 0.054665 | PMM |
| 102 | HE160A | Column | No Messages | 0.040064 | PMM |
| 103 | HE160A | Column | No Messages | 0.261971 | PMM |
| 104 | HE160A | Column | No Messages | 0.406105 | PMM |
| 105 | HE140A | Beam | No Messages | 0.162303 | PMM |
| 106 | HE140A | Beam | No Messages | 0.131533 | PMM |
| 107 | HE140A | Beam | No Messages | 0.211858 | PMM |
| 108 | HE140A | Beam | No Messages | 0.251346 | PMM |
| 109 | HE140A | Beam | No Messages | 0.171418 | PMM |
| 110 | HE140A | Beam | No Messages | 0.146359 | PMM |
| 111 | HE140A | Beam | No Messages | 0.273511 | PMM |
| 112 | 2UPN120-12 | Brace | No Messages | 0.375081 | PMM |
| 113 | 2UPN120-12 | Brace | No Messages | 0.19283 | PMM |
| 114 | 2UPN120-12 | Brace | No Messages | 0.182065 | PMM |
| 115 | 2UPN120-12 | Brace | No Messages | 0.451008 | PMM |
| 116 | 2UPN120-12 | Brace | No Messages | 0.20756 | PMM |
| 117 | 2UPN120-12 | Brace | No Messages | 0.417087 | PMM |
| 118 | 2UPN120-12 | Brace | No Messages | 0.171919 | PMM |
| 119 | HE120A | Beam | No Messages | 0.13618 | PMM |
| 120 | IPE120 | Brace | No Messages | 0.064215 | PMM |
| 121 | HE120A | Beam | No Messages | 0.137819 | PMM |
| 122 | IPE120 | Brace | No Messages | 0.064216 | PMM |
| 123 | HE120A | Beam | No Messages | 0.139296 | PMM |
| 124 | IPE120 | Brace | No Messages | 0.064217 | PMM |
| 125 | HE120A | Beam | No Messages | 0.139809 | PMM |
| 126 | IPE120 | Brace | No Messages | 0.064216 | PMM |
| 127 | UPN140 | Beam | No Messages | 0.12311 | PMM |
| 128 | UPN140 | Beam | No Messages | 0.132319 | PMM |
| 129 | L60X6 | Beam | No Messages | 0.122285 | PMM |
| 130 | L60X6 | Beam | No Messages | 0.122288 | PMM |
| 131 | UPN140 | Beam | No Messages | 0.12312 | PMM |
| 132 | UPN140 | Beam | No Messages | 0.132382 | PMM |
| 133 | L60X6 | Beam | No Messages | 0.122283 | PMM |
| 134 | L60X6 | Beam | No Messages | 0.122287 | PMM |
| 135 | L60X6 | Beam | No Messages | 0.021851 | PMM |
| 136 | L60X6 | Beam | No Messages | 0.021851 | PMM |
| 137 | HE120A | Beam | No Messages | 0.037961 | PMM |
| 138 | HE120A | Beam | No Messages | 0.040573 | PMM |
| 139 | IPE120 | Beam | No Messages | 0.017324 | PMM |
| 140 | IPE120 | Beam | No Messages | 0.02021 | PMM |
| 141 | IPE120 | Beam | No Messages | 0.022546 | PMM |
| 142 | IPE120 | Beam | No Messages | 0.014772 | PMM |
| 143 | IPE120 | Beam | No Messages | 0.031597 | PMM |
| 144 | IPE120 | Beam | No Messages | 0.025976 | PMM |
| 145 | IPE120 | Beam | No Messages | 0.021312 | PMM |
| 146 | IPE120 | Beam | No Messages | 0.036496 | PMM |
| 147 | HE160A | Column | No Messages | 0.275513 | PMM |

Table:  Steel Design 1 - Summary Data - AISC 360-16, Part 2 of 2

| Table: Steel Design 1 - Summary Data - AISC 360-16, Part 2 of 2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frame | Combo | Location | ErrMsg | WarnMsg |
|  |  | m |  |  |
| 99 | ES_COMB11 | 2.6 | No Messages | No Messages |
| 101 | ES_COMB16 | 0 | No Messages | No Messages |
| 102 | COMB08 | 2.5 | No Messages | No Messages |
| 103 | ES_COMB10 | 2.6 | No Messages | No Messages |
| 104 | ES_COMB13 | 2.6 | No Messages | No Messages |
| 105 | ES_COMB16 | 1.8 | No Messages | No Messages |
| 106 | ES_COMB11 | 1.85 | No Messages | No Messages |
| 107 | ES_COMB09 | 1 | No Messages | No Messages |
| 108 | ES_COMB12 | 1 | No Messages | No Messages |
| 109 | ES_COMB12 | 1.85 | No Messages | No Messages |
| 110 | ES_COMB10 | 1 | No Messages | No Messages |
| 111 | ES_COMB14 | 1.8 | No Messages | No Messages |
| 112 | ES_COMB10 | 2.87761 | No Messages | No Messages |
| 113 | ES_COMB11 | 2.87761 | No Messages | No Messages |
| 114 | ES_COMB13 | 2.86531 | No Messages | No Messages |
| 115 | ES_COMB14 | 2.86531 | No Messages | No Messages |
| 116 | ES_COMB16 | 0 | No Messages | No Messages |
| 117 | ES_COMB09 | 2.87761 | No Messages | No Messages |
| 118 | ES_COMB11 | 2.87761 | No Messages | No Messages |
| 119 | ES_COMB15 | 0.65 | No Messages | No Messages |
| 120 | COMB10 | 0.98995 | No Messages | No Messages |
| 121 | ES_COMB13 | 0.65 | No Messages | No Messages |
| 122 | COMB10 | 0.98995 | No Messages | No Messages |
| 123 | ES_COMB14 | 0.65 | No Messages | No Messages |
| 124 | COMB11 | 0.98995 | No Messages | No Messages |
| 125 | ES_COMB16 | 0.65 | No Messages | No Messages |
| 126 | COMB11 | 0.98995 | No Messages | No Messages |
| 127 | COMB02 | 1.4 | No Messages | No Messages |
| 128 | COMB02 | 1.4 | No Messages | No Messages |
| 129 | ES_COMB13 | 0.79412 | No Messages | No Messages |
| 130 | ES_COMB16 | 0.79412 | No Messages | No Messages |
| 131 | COMB02 | 1.4 | No Messages | No Messages |
| 132 | COMB02 | 1.4 | No Messages | No Messages |
| 133 | ES_COMB14 | 0.79412 | No Messages | No Messages |
| 134 | ES_COMB15 | 0.79412 | No Messages | No Messages |
| 135 | ES_COMB09 | 0.375 | No Messages | No Messages |
| 136 | ES_COMB12 | 0.375 | No Messages | No Messages |
| 137 | COMB11 | 1.425 | No Messages | No Messages |
| 138 | COMB11 | 1.425 | No Messages | No Messages |
| 139 | ES_COMB10 | 0.4714 | No Messages | No Messages |
| 140 | ES_COMB11 | 0.4714 | No Messages | No Messages |
| 141 | ES_COMB09 | 0.94281 | No Messages | No Messages |
| 142 | ES_COMB12 | 0.4714 | No Messages | No Messages |
| 143 | ES_COMB12 | 0.4714 | No Messages | No Messages |
| 144 | ES_COMB09 | 0.94281 | No Messages | No Messages |
| 145 | ES_COMB11 | 0.4714 | No Messages | No Messages |
| 146 | ES_COMB10 | 0.4714 | No Messages | No Messages |
| 147 | ES_COMB14 | 2.6 | No Messages | No Messages |

12.  Story Drift & Deflection Control

According to ASCE7-16 Table 12.12-1 :

Allowable Story Drift For I & II Stroy = 0.025h

→ Cd*eu< 0.025*h  → eu< 0.025*5000/3. 5 → eu< 35.7 mm

Cd=3. 5

Maximum Drift at 160 joint in Direction x = 1.61 mm < 35.7 mm ………………………………… (OK)

Maximum Drift at 160 joint in Direction y = 2.2 mm < 35.7 mm ………………………………… (OK)

DEFLECTION CONTROL:

Main Beam: Dmaximum =0.289 cm<L/500 (L=280)

Walkway Beam: Dmaximum =0.16 cm<L/300 (L=400)