## REPLY SHEET
CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Comment / Reply Sheet
Comment / Reply Sheet No.: |  | EI027-DMF-VD-EL-DSH-017-R0 |  | Document Description: |  | Electrical Motor Data Sheet
Reply Sheet Date: |  | 2024-08-11 |  | Document No.: |  | EI027-DMF-VD-EL-DSH-017
Transmittal No.: |  | TR-022 |  | Document Revision: |  | R0
Item No. | Comments |  |  |  | Vendor Clarifications
1 | Tag numbers to be specified |  |  |  | Please specify tag numbers of motors ENER Reply: RU0001A-M-02,RU0001A-M-03 /RU0001B-M-02,RU0001B-M-03 Please modify GAD as per these tag numbers too
2 | cable sizes shall be as per current |  |  |  | Please specify cable type and size and cable gland ENER Reply: min. cable sizes shall be specified as per current by vendor (Distance to MCC is approximately 500 m)
According to the availability of electric motors with RAL-5010 and contrary to the project spec, which RAL-5015 is acceptable, please confirm the electric motors. ENER Reply: Confirmed
Legend of Document Status:
CO: Commented |  |  | AN: Approved as Noted
AP: Approved |  |  | RE : Rejected
6
NDEC
NDEC