Dear Sir,

As discussed, Kindly find below the price offer.

Item no.1 Part No. CTB484820S1. (RU001A-LCP-01 & RU001B-LCP-01))

Junction box is made in stainless steel 316L. Ex II 2GD Ex deb IIC T Gb Ex tb IIIC T°C Db, IP66.

Delta Comment: Component to be Exd rated and local panel to be Exe. Please confirm.

Ambient temperature -20 +55°C. Lid fixed with hinges and screws.

1 removable gland plate: bottom side. External dimension 480x480x205mm.

1xSS mounting plate.

1x SS breather with Lock Nut.

5x 24V DC Indicating lamp. (Please confirm the color of the each lamp)

Delta Comment:

- Common Alarm Unit: Yellow

- Common Trip Unit: Red

- Unit Ready to Start: Green

- Compressor Running: Green

- Oil Pump Running: Green

3x Green Pushbutton with 1NO contact block.

Delta Comment:

2x Green Pushbutton with 2NO contact block.

- Unit Start

- Oil Pump Start

3 x Red Push button with 1NC contact block.

Delta Comment:

2 x Red Push button with 2NC contact block.

- Unit Stop

- Oil Pump Stop

For Emergency Push Botton:

RED/Yellow EM push button with 4NC Contact block complete with protection shroud

For Lamp Test:

1 x Black push button with 2NO Contact block

2x 10A 2 POSITION (L-A/R)Selector switch with external handle.

2x 10A 3 POSITION (H-O-A)Selector switch with external handle.

TB-1: 12x2.5sq.mm terminal.(WDU2.5)

TB-2: 12x2.5sq.mm terminal.(WDU2.5)

TB-3: 12x2.5sq.mm terminal.(WDU2.5)

TB-4: 12x2.5sq.mm terminal.(WDU2.5)

4X M25x1.5 Brass Ni-Plated Cable Gland with Lock-Nut.

1X M40x1.5 Brass Ni-Plated Cable Gland with Lock-Nut.

Delta Comment:

Please consider the M40 entry with Brass Ni-Plated stopping plug

Please add two M32 with Brass Ni-Plated stopping plug

Cable entry details.(Please confirm the cable entry)

1x41mm hole suitable for M40 cable entry at the bottom.

Delta Comment:

Please consider two M32 cable entry hole

4x26mm hole suitable for M25 cable entry at the bottom.

https://pim.cortemgroup.com/uploads/pim/originals/13-ctb-en.pdf

Delta Comment:

1x Earth bar with M5 with 10 holes.

Unit Price in Euro: 2,500.00.

Qty: 2 Nos.

Total in Euro: 5,000.00.

Item no.2:- PART NO.: CTB453820S1. (JBD-A-RU0001A-01 & JBD-A-RU0001B-01)

Junction box made in stainless steel 316L. Ex II 2GD Ex eb IIC T Gb Ex tb IIIC T°C Db, IP66.

Ambient temperature -20 +55°C. Lid fixed with hinges and screws.

1 removable gland plate: bottom side. External dimension 450x380x205mm.

1 x SS Mounting Plate.

1 X M8 Earthing stud.

1x M20x1.5 SS SS with Locknut.

Delta Comment:

Please confirm you mean breather

TB-1: 24x2.5sq.mm terminal.(WDU2.5)

TB-2: 12x2.5sq.mm terminal.(WDU2.5)

Delta Comment:

TB-2: 21x2.5sq.mm terminal.(WDU2.5)

2x M20x1.5 Brass Ni-Plated stopping plug with lock-nut.

Cable entry details. (Please confirm the cable entry)

1x26mm hole suitable for M25 cable entry at the bottom.

15x221mm hole suitable for M20 cable entry at the bottom.

https://pim.cortemgroup.com/uploads/pim/originals/14-ctb_en.pdf

Delta Comment:

1x Screen Bar with earth bolt.

10X M20x1.5 Brass Ni-Plated Cable Gland with Lock-Nut.

2 X M20x1.5 Brass Ni-Plated stopping plug with lock-nut.

1X M25x1.5 Brass Ni-Plated  stopping plug  with Lock-Nut.

1X M32x1.5 Brass Ni-Plated stopping plug  with Lock-Nut.

Unit Price in EURO: 1,250.00

Qty: 2 Nos.

Total Price in EURO: 2,500.00

Item no.3:- PART NO.: CTB303020S1.(JBD-A-RU0001A-03 & JBD-A-RU0001B-03)

Junction box made in stainless steel 316L. Ex II 2GD Ex eb IIC T Gb Ex tb IIIC T°C Db, IP66.

Ambient temperature -20 +55°C. Lid fixed with hinges and screws.

1 removable gland plate: bottom side. External dimension 306x306x205mm.

1 x SS Mounting Plate.

1 X M8 Earthing stud.

1x M20x1.5 SS SS with Locknut.

Delta Comment:

Please confirm you mean breather

TB-1: 30x2.5sq.mm terminal.(WDU2.5)

Delta Comment:

Please consider TB-1: 12x2.5sq.mm terminal.(WDU2.5)

2x M20x1.5 Brass Ni-Plated stopping plug with lock-nut.

Delta Comment:

1x Screen Bar with earth bolt.

2 X M20x1.5 Brass Ni-Plated Cable Gland with Lock-Nut.

2 X M20x1.5 Brass Ni-Plated stopping plug with lock-nut.

1X M25x1.5 Brass Ni-Plated  stopping plug with Lock-Nut.

Cable entry details. (Please confirm the cable entry)

1x26mm hole suitable for M25 cable entry at the bottom.

10x221mm hole suitable for M20 cable entry at the bottom.

Delta Comment:

4 X M20x1.5 hole suitable for M20 cable entry at the bottom.

1X M25x1.5 hole suitable for M25 cable entry at the bottom.

https://pim.cortemgroup.com/uploads/pim/originals/14-ctb_en.pdf

Unit Price in EURO: 800.00

Qty: 2 Nos.

Total Price in EURO: 1,600.00

Item no.4:- PART NO.: CTB262620S1.(JBD-A-RU0001A-02 & D-A-RU0001B-02)

Junction box made in stainless steel 316L. Ex II 2GD Ex eb IIC T Gb Ex tb IIIC T°C Db, IP66.

Ambient temperature -20 +55°C. Lid fixed with hinges and screws.

1 removable gland plate: bottom side. External dimension 260x260x205mm.

1 x SS Mounting Plate.

1 X M8 Earthing stud.

1x M20x1.5 SS SS with Locknut.

Delta Comment:

Please confirm you mean breather

TB-1: 16x2.5sq.mm terminal.(WDU2.5)

2x M20x1.5 Brass Ni-Plated stopping plug with lock-nut.

Delta Comment:Please add following items

5 X M20x1.5 Brass Ni-Plated Cable Gland with Lock-Nut.

1X M25x1.5 Brass Ni-Plated stopping plug with lock-nut.

1X M32 x1.5 Brass Ni-Plated stopping plug with lock-nut.

Cable entry details. (Please confirm the cable entry)

1x26mm hole suitable for M25 cable entry at the bottom.

12x221mm hole suitable for M20 cable entry at the bottom.

Delta Comment:Please add following items

7 X hole suitable for M20 cable entry at the bottom

1X hole suitable for M25 cable entry at the bottom

1X hole suitable for M32 cable entry at the bottom

https://pim.cortemgroup.com/uploads/pim/originals/14-ctb_en.pdf

Unit Price in EURO: 600.00

Qty: 2 Nos.

Total Price in EURO: 1,200.00

Item no.5:- PART NO.: CTB262620S1.(JBD-A-RU0001A-04 & JBD-A-RU0001B-04)

Junction box made in stainless steel 316L. Ex II 2GD Ex eb IIC T Gb Ex tb IIIC T°C Db, IP66.

Ambient temperature -20 +55°C. Lid fixed with hinges and screws.

1 removable gland plate: bottom side. External dimension 260x260x205mm.

1 x SS Mounting Plate.

1 X M8 Earthing stud.

1x M20x1.5 SS SS with Locknut.

Delta Comment:

Please confirm you mean breather

TB-1: 16x2.5sq.mm terminal.(WDU2.5)

Delta Comment:

Please  consider TB-1: 12x2.5sq.mm terminal.(WDU2.5)

2x M20x1.5 Brass Ni-Plated stopping plug with lock-nut.

Delta Comment:

Please add following items

4 X M20x1.5 Brass Ni-Plated Cable Gland with Lock-Nut.

1X M25x1.5 Brass Ni-Plated stopping plug with lock-nut.

1X M32 x1.5 Brass Ni-Plated stopping plug with lock-nut.

Cable entry details. (Please confirm the cable entry)

1x26mm hole suitable for M25 cable entry at the bottom.

12x21mm hole suitable for M20 cable entry at the bottom.

Delta Comment:

6 X hole suitable for M20 cable entry at the bottom

1X hole suitable for M25 cable entry at the bottom

1X hole suitable for M32 cable entry at the bottom

https://pim.cortemgroup.com/uploads/pim/originals/14-ctb_en.pdf

Unit Price in EURO: 600.00

Qty: 2 Nos.

Total Price in EURO: 1,200.00

Item no.6 Part No. CTB221513S1.(TB-HTR-RU0001A & TB-HTR-RU0001B)

Delta Comment:

Please delete these TB-HTR-RU0001A & TB-HTR-RU0001B from scope of supply.

Junction box made in stainless steel 316L. Ex II 2GD Ex- deb IIC T Gb Ex tb IIIC T°C Db, IP66.

Ambient temperature -20 +55°C. Lid fixed with hinges and screws.

1 removable gland plate: bottom side. External dimension 229x152x130mm.

1 x SS mounting plate

1x M20x1.5 SS SS with Locknut.

2xGreen Pushbutton with 1NO contact block.

2x M20x1.5 BNP plug with lock-nut.

4x2.5sq.mm terminal (WDU2.5)

Cable entry:

3-21mm hole suitable for M20 at the bottom side.

https://pim.cortemgroup.com/uploads/pim/originals/13-ctb-en.pdf

Unit Price in Euro: 500.00.

Qty: 2 Nos.

Total in Euro: 1,000.00.

Terms & Conditions:

1.            Payment: 100% along with the Purchase Order

2.             The prices quoted are for Ex-works Jafza, UAE, It doesn't include VAT + Customs clearance + Documentation + Delivery.

3.            Delivery Time: The estimated delivery time will be 4-5 working weeks from that date of PO and approved GA drawing

4.             Our Tax Registration No. (TRN) 100380564300003.

5.             Offer Validity: 30 days

6.             Please note that if the order value is less than EUR 300, then a surcharge of EUR 50 is added to the original amount.

7.             70 extra for COO for attested.

8.             If inspection is applicable then TPI will be under your scope and there will 500 euro service charge per day.

Should you have any queries, please feel free to contact us.