STYRENE PARK OFFSITE Document Title: ??????????

| Rev. | Issued Date | DESCRIPTION | PREPARED | CHECKED | APPROVED |
| --- | --- | --- | --- | --- | --- |

REVISION RECORD SHEET

| Page Page | Revisions |  |  |  |  |  |  |  | Page | Revisions |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |  |  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |
| 1 | × | × |  |  |  |  |  |  | 41 |  |  |  |  |  |  |  |
| 2 | × | × |  |  |  |  |  |  | 42 |  |  |  |  |  |  |  |
| 3 | × |  |  |  |  |  |  |  | 43 |  |  |  |  |  |  |  |
| 4 | × |  |  |  |  |  |  |  | 44 |  |  |  |  |  |  |  |
| 5 | × |  |  |  |  |  |  |  | 45 |  |  |  |  |  |  |  |
| 6 | × |  |  |  |  |  |  |  | 46 |  |  |  |  |  |  |  |
| 7 | × |  |  |  |  |  |  |  | 47 |  |  |  |  |  |  |  |
| 8 | × |  |  |  |  |  |  |  | 48 |  |  |  |  |  |  |  |
| 9 | × |  |  |  |  |  |  |  | 49 |  |  |  |  |  |  |  |
| 10 | × |  |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  |
| 11 | × |  |  |  |  |  |  |  | 51 |  |  |  |  |  |  |  |
| 12 | × |  |  |  |  |  |  |  | 52 |  |  |  |  |  |  |  |
| 13 | × |  |  |  |  |  |  |  | 53 |  |  |  |  |  |  |  |
| 14 | × |  |  |  |  |  |  |  | 54 |  |  |  |  |  |  |  |
| 15 | × |  |  |  |  |  |  |  | 55 |  |  |  |  |  |  |  |
| 16 | × |  |  |  |  |  |  |  | 56 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  | 57 |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  | 58 |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  | 59 |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  | 60 |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  | 61 |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  | 62 |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  | 63 |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  | 64 |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  | 66 |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  | 67 |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  | 68 |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  | 69 |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  | 70 |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  | 71 |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |  | 72 |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  | 73 |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |  | 74 |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  | 75 |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |  | 76 |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |  | 77 |  |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  |  | 78 |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |  | 79 |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |  | 80 |  |  |  |  |  |  |  |

Table of Contents

1.0	Introduction	4

2.0	Scope	4

3.0	NORMATIVE REFERENCES	4

4.0	IG-55 EXTINGUISHING SYSTEM	5

4.2.1	GENERAL	7

4.2.2	CYLINDERS	7

4.2.3	ACTUATOR VALVES	7

5.0	AUDIBLE AND VISUAL ALARMS	8

6.0	IG-55 CONTROL PANEL	9

7.0	SCOPE OF SUPPLY	9

8.0	INSTRUMENTATION, PIPEWORK AND VALVES	10

9.0	MAINTENANCE	11

10.0	PAINT AND FINISHING	11

11.0	TESTING	11

12.0	INSPECTION	13

13.0	TRANSITION	13

14.0	GUARANTEE	14

15.0	IG-55 control SYSTEM SKETCH	14

16.0	IG-55 DEMAND CALCULATION	14

- Introduction

Creation and development of chain units of Styrene Monomer is the mission of Gohar Ofogh Industrial Park. This Company joint investment of four companies including JPC, Asaluyeh Sadaf Chemical, Kimia Sanaye Dalahoo and Entekhab Group and is located in Assaluyeh.

Feed and utility lines and network construction, a Styrene Monomer tank construction, Peroxide and its sidelong equipment warehouse are among this company ̓s missions.

Some of the ongoing Projects of this company are:

- ABS-Rubber project

- ESBR project

- EPS project

- Poly Styrene

Utility services of Park Styrene, including DM water, HP steam, service water, potable water, cooling water make up, nitrogen, instrument air, plant air and fuel gas are provided by Damavand Petrochemical and delivered at the south battery limit of park styrene. COC, POC, SN, Condensate return and cooling blow down are returned from park styrene and return to Damavand Petrochemical.

- Scope

Purpose of this specification is to define the “Clean Agent System Demand Calculation and Specification” for the project .It shall be used in conjunction with data/requisition sheets for present document subject.

- NORMATIVE REFERENCES

  - INTERNATIONAL CODES AND STANDARDS

- NFPA 2001	Clean		Agent Fire Extinguishing Systems (2013 Edition)

- ISO 14520-1		Gaseous fire – extinguishing systems

  - ORDER OF PRECEDENCE

In case of contradiction, the following order of precedence shall apply:

- Data Sheets / Drawings

- This Document

- The Other Project Documents Listed Above

- IPS

- Other Local Codes and Standards

- International Codes and Standards

  - ABBREVIATIONS

| IG | Inert Gas |
| --- | --- |
| ODP | Ozone Depletion Potential |
| GWP | Global Warming Potential |
| HVAC | Heating Ventilation and Air Conditioning |
| F&G | Fire & Gas |

- IG-55 EXTINGUISHING SYSTEM

  - Basis of Design

The extinguishing agent shall be IG-55 which meets NFPA 2001 specification.

ARGOGEN (IG-55) is a fast clean extinguishing agent. Its constituents are naturally occurring gases, Argon and Nitrogen. (Chemical compound designation IG55) It is approved for use in normally occupied areas and perfectly safe for human exposure at the system design concentrations. It is stored at 200 and 300 BAR pressure as a gas in standard size cylinders. The ARGOGEN is discharged through a piping network into the protected area.

Both Argon and Nitrogen are clean, natural gases that are readily available naturally in the atmosphere, so it is safe for use in a wide range of sensitive applications where people are present. IG55 is an inert gas that extinguishes fire based on the principle of oxygen depletion. IG55 is an  environmentally acceptable clean agent that offers Zero Ozone Depletion Potential (ODP) and Zero Global  Warming Potential (GWP). IG55 is electronically non-conductive, colorless, odorless and flavorless. It is non corrosive and may be used at normal temperatures with such materials as nickel, steel, stainless steel, copper, brass, bronze and plastics. Perfect dielectric and appropriate for the protection of all the electric and electronic  materials. IG55 produces no post fire residue: thus, there is no damage to protected equipment and nothing toclean up. IG55 extinguishes fire by physically removing oxygen from the atmosphere. In occupied areas, people can breathe IG55 at extinguishing concentrations without fear. There are no toxicological factors  associated with the use of IG55 and it will not decompose or produce any by-products when exposed to a flame from a fire condition. IG55 is suitable for fighting fires in confined spaces. Because its molecular weight is close to that of air, it lingers longer when discharged to extinguish a fire. This reduces the need for hermetic sealing of a protected room – a process that can be very expensive. When a fire starts, IG55 is injected rapidly into the room, reducing the oxygen level from the normal 21% to between 11% and 13%. This is too low for further combustion to take place, yet high enough to allow essential safety personnel to operate.

The detection system for each protected room consists of one detection loop or part of one loop with point addressable smoke or heat detectors.

When two smoke or heat detectors installed in the protected areas are activated, Fire & Gas Control Panel will send a signal to HVAC control panel to stop ventilation in Rooms and close the dampers and release IG-55 after adequate time delay.

Operator in Control Room could be interface between Detection and Extinguishing System, and by manual triggering of the Extinguishing System, shall ensure personnel protection against extinguishing gas release effects. Mobile equipment (breathing apparatus) shall be readily available in protected areas, to allow permanent presence in these protected rooms. Prior to initiation of Extinguishing System the dampers will be closed.

The extinguishing system shall be provided for all protected rooms in this area.

The Extinguishing system shall consist of one battery of cylinders designed for 100% fire protection. The system shall be a total flooding type with the following performance capabilities:

- Time delay: IG-55 shall be released only after the activation of visual and audible alarms in the protected room to allow people to evacuate. For this purpose, an adjustable time delay up to 60 seconds shall be provided.

- Discharge time: the discharge time required to achieve 95 percent of the minimum design concentration for flame extinguishment shall not exceed 120 seconds for Class A surface fire hazards or Class C hazards, or as otherwise required by the authority having jurisdiction.

- Design concentration: The design concentration shall be maintained in the protected rooms as per NFPA 2001.

- Holding time: The holding time shall be 10 minutes. It is essential to determine the likely period during which the extinguishing concentration will be maintained within the protected enclosure. This is known as the hold time.

- Exposure Time: The maximum exposure time in any case shall not exceed 5 minutes. Unnecessary exposure to inert gas agent systems resulting in low oxygen atmospheres shall be avoided. Inert gas systems designed to concentrations below 43 percent (corresponding to an oxygen concentration of 12 percent, sea level equivalent of oxygen) shall be permitted where means are provided to limit exposure to no longer than 5 minutes. The system shall be hydraulically designed, engineered, manufactured, tested and installed for total flooding protection according to NFPA 2001 and ISO 14520.

  - Extinguishing Agent Cylinders and Accessories

### GENERAL

- Cylinders, accessories and the distribution system shall comply with NFPA 2001.

- IG-55 shall be stored in high pressure cylinders of standard type and shall be of same size.

- Cylinders shall be installed in IG55 Closure Room in the safe cabinet.

- Initiation of the system shall be automatically or manual: manual initiation by means of a push button in Control Room and Mechanical manual release on cylinder rooms.

### CYLINDERS

- Sufficient extinguishing agent shall be for one extinguishing discharge in each room. 1 x 100% spare shall be provided.

- Each cylinder shall be equipped with pneumatic Discharge Valve which is interconnected to others in order to activate immediately.

- Each cylinder shall be equipped with a pressure gauge and pressure switch Low.

### ACTUATOR VALVES

- Actuator valves shall be mounted on top of the cylinders and connected to a manifold.

- Actuator valve of the cylinder, or pilot cylinder in case of more than one cylinder per protected room, shall be designed for the agent release by an electric triggering valve with a pin to perform test on valve without any discharge.

  - Cylinder manifold

- The cylinder manifold shall interconnect group of cylinders. Flexible hoses shall be used between the storage cylinder and the manifold and shall be of approved materials and suitable for service at the anticipated pressure and maximum and minimum temperatures.

- The restrictor consists of an orifice with a well-defined flow resistance characteristic shall be mounted as close as possible to the manifold in order to reduce the extent of high pressure pipe installation.

- Check valves shall prevent agent loss during discharge or when a cylinder is disconnected from the manifold.

- Access for easy maintenance, removal and replacement of the valving, manifold assembly and each cylinder shall be foreseen.

- All fittings necessary for complete installation shall be provided.

- Discharge pressure switch shall be provided downstream of restrictor.

  - Extinguishing Nozzles and Piping

Nozzles and piping shall be designed and made of materials in accordance with NFPA 2001 and appropriate for site conditions specified in the project documents. The Number of nozzles shall be defined by VENDOR after finalization of P&ID for Inert Gas.

  - IG-55 Cylinder Reserve

Quantity of IG-55 cylinder will be considered 100% as standby. Only one cylinder size shall be used at site.

Spares cylinders used for reserve shall be charged with 100% filling capacity corresponding to duty cylinders filling capacity installed on site. Manual switching facility shall be provided.

The VENDOR will assure that no physical harm can be done to Personnel due to high IG-55 concentration (the concentration of IG-55 has not to exceed 52%) in case of using the reserve cylinders with charged fill capacity greater than cylinder fill capacity for the room.

  - Pressure Relief Valve

Pressure relief device should be fitted downstream of restrictor so that discharge, in the event of operation, will not injure or endanger personnel.

  - Instrumentation

All instrumentation on cylinders and associated valves shall be in accordance with NFPA 2001.

  - Directional Valves (if applicable)

Directional valve will be installed in the discharge piping downstream of the agent containers, to direct the agent to the appropriate hazard enclosure by the mean of solenoid valve.

- AUDIBLE AND VISUAL ALARMS

The audible alarm shall operate for 30 seconds prior to release and continue for 45 seconds, after which it may be silenced from the local panel. Also, Audible and visual alarms shall be provided outside the protected area for release warning.

- IG-55 CONTROL PANEL

  - General Description

An IG-55 Control Panel (see appendix 1) shall be provided for the system in Control Room. The IG-55 Control Panel shall control the agent release. In the automatic mode, it shall receive actuation signals from F&G system and shall send alarms and system fault signals to the F&G system. The IG-55 control system shall be micro processing type.

IG-55 Control Panels shall include:

- Switch with four following positions :

- Automatic mode

- Manual mode

- Inhibit

- Maintenance override

- Four colored status lamps :

- Green: 	inhibit

- Amber: 	manual mode

- Blue: 	Automatic mode

- Red: 	IG-55 release

- A push button to manually release the IG-55

All the IG-55 Control Panels shall be fed by power supply 110 VAC–50 Hz from UPS. All other voltage requirements shall be derived from this voltage by vendor. All information shall be written in English.

  - Inhibit

This facility is used during maintenance operation only to prevent any release of IG-55 except the local mechanical release at the IG-55 Cylinder Storage.

The inhibition command facility provided on the IG-55 Control Panel allows the inhibition of the manual/Automatic release signals and prevent the activation of the solenoid valve and audible alarms.

  - Maintenance Override

A maintenance override (pin system) shall be provided on the IG-55 actuator valve. Its purpose is to perform verification tests of system elements without IG-55 release.

- SCOPE OF SUPPLY

The IG-55 VENDOR shall design, supply and install the entire system including but not limited to:

- Cylinders with a quantity of IG-55 for one discharge for each room and a reserve of IG-55 cylinders

- Cylinders racks

- Pressure gauges, Pressure switch Low, Discharge Pressure switches.

- Piping, nozzles, Bolts, nuts, clamps, gaskets etc. Manifolds and accessories as specified and complete to provide an operational system.

- All required instrumentation & Hook-up.

- Restrictors, directional valves, Pressure relief devices.

- All required Actuation system.

- Terminal junction box receiving transmission of 24 volt DC signals.

- Micro Processor IG-55 Control Panel (with provision for input / output signals).

- All operating devices which are necessary to match with required alarms and F&G system.

The VENDOR shall provide a complete documentation of the system in accordance with Section 6 of NFPA 2001 for Contractor’s approval. This shall include but not limited to the following:

- IG-55 mechanical and instrument components data sheets.

- System assembly and connection drawings shall be provided. The drawings shall show component dimensions and weights. These shall include pressure switches, line size, hanger and support arrangement, nozzle location, type and orifice size.

- Drawings shall be provided showing the size, location and arrangement of the discharge nozzles, IG-55 cylinders, control / release valves, cylinder manifold and cylinder mounting, and for the manual actuation lever, warning lamps and horn.

- Piping isometrics.

- Calculation sheets.

- One line diagram if electrical supply and connection of all the parts of the system and writing diagram.

- Maintenance & Test procedures and spare parts list.

- Operating manuals for all the equipment.

- Cables writing diagram of the system.

- INSTRUMENTATION, PIPEWORK AND VALVES

The supply shall include all the necessary instruments, electric and or pneumatic materials, equipment, etc. to ensure a good and safe operation considering codes and standards .The piping supply (pipes, flanges valves, fittings and Relevant support bracket, etc.) should cover all interconnecting with the package B.L Special corrosion–resistant material or coatings shall be used in highly corrosive atmosphere.

- MAINTENANCE

Maintenance instructions, periodical inspections and manual/remote and automatic operation of system should be furnished and included with package of system supplied.

- PAINT AND FINISHING

Paints and finishes shall be durable Manufacturer’s standard and shall adequately protect all pieces from their environment. However, severe corrosive elements shall be considered and the equipment shall be painted with proper corrosion resistant primer and final coating for hot, humid, corrosive and unshaded conditions.

Surfaces shall be clean, dry and free from dust and grease before painting.

- TESTING

A: General

- The system shall be tested according to Section 4.7 of NFPA 2001 without IG-55 discharge and with nonhazardous / un-harmful Testing gas.

- The MANUFACTURER shall quote all his normal tests required as well as hydrostatic, simulation and functional tests specified below. MANUFACTUER shall conduct these tests with the same materials for seal and other parts which have been sold to the OWNER.

- A test record shall be made and shall include all descriptive or pertinent information to identify the system. The test information as specified below shall be provided in a letter of certification that the system was tested and met the requirements of this specification.

- The simulation test shall consist of actuating the system under a no-flow condition to verify unit compatibility of the complete assembly.

- All valves shall be subjected to a hydrostatic shell test in accordance with the applicable code. No visible leakage through valve’s seat is permitted when the valve is in close position.

- All pressurized parts of the system shall be subjected to hydrostatic test at a pressure not less than one and a half times the design pressure of that part.

- Prior to shipment, VENDOR shall submit, an operational test simulating actual design operating conditions as closely as possible. VENDOR shall conduct this test in presence of OWNER unless a written waiver is given.

- OWNER shall have, notification of VENDOR test 30 days prior to test date.

- Defective parts, if present, shall be replaced with new parts and system retested until completely reliable and accepted.

- VENDOR shall furnish all equipment, material and labor required for the test.

- The VENDOR shall issue instruction of the proper initial and period testing of the installed system and shall provide any special equipment required for calculation and testing during operation of the system.

- Test information and results as specified below shall be provided in a letter certifying that the system was tested and all requirements specified.

It shall include:

- Date of test

- Purchase order, item numbers, tag numbers

- Transition destination

- Equipment serial number(s)

- Signature of Manufacturer’s test witness and/or OWNER representative

- Test procedure(s)

- Officially certified summary of test observation results and conclusions.

Any malfunctions and/or system corrections shall be reported. In addition video tape of the system shall be furnished during test.

B: FACTORY TEST

Checking of correct assembly, complete electrical testing, and operation of the discharge mechanisms (both automatic and manual) shall be carried out at the factory and before shipping.

This test shall be carried out using a cylinder with air or nitrogen compressed to the maximum extinguishing agent pressure (at maximum temperature). Adequate cylinder opening operation at maximum back-pressure shall also be tested.

C: PRELIMINARY ACCEPTANCE TEST

A second test shall be carried out, in operating conditions, with the Inert Gas cylinders connected to the network. Discharge test is not required. This test shall be carried out at site. The purpose of this test is to ensure that all piping, nozzles, cylinders and auxiliary devices have been installed in accordance with VENDOR's recommendations and approved drawings.

The following operating parameters as a minimum should be monitored and checked during the test:

- effective time delay,

- operation of visual and audible alarms,

- correct feedback of signals to the control panel,

- correct operation of interlocks, inhibits and overrides,

- Correct operation of test facility.

- INSPECTION

- OWNER authorized representative shall be afforded the opportunity to witness the manufacturing, testing and assembling any part of the VENDOR which concerns the system ordered.

- The VENDOR shall agree, by his acceptance of the Purchase order to an inspection and rejection stipulations in accordance with standard practices and codes specified herein.

- Before final assembly, pipe and fittings shall be inspected visually to ensure they are clean and free of burrs, spelter and dust, and that no foreign matter is inside and the full bore is clear.

- Any Inspection and testing in no way relieve the VENDOR of any responsibility for the system meeting all requirements of this specification and applicable codes.

- The VENDOR shall issue instructions for the proper inspection system, according to acceptable international and NFPA standards.

- TRANSITION

Skid package unit and related equipment shall be properly prepared for transit to prevent damage from handling, warehousing or transition and shall be labeled to insure is not lost in transit. In addition, the following measures shall be taken.

- All external connections shall be protected by temporary closures to exclude dirt and other foreign matter.

- One packing list to be included inside every package (box) and one packing list to be in a metal enclosure attached to the package.

- Adequate transition supports and packing shall be provided in order to prevent external damage during transit. For ocean transport, the equipment shall be crated in heavy duty, container sealed with strong tape or metal bands. Also provisions shall be taken to protect the equipment from possible marine exposure.

- GUARANTEE

Vendor shall also warrant engineering, materials and workmanship of equipment for a period of 18 months after successful start-up or 24 months after shipping. Under this warranty, all materials, parts and assemblies found to be defective during the guarantee period shall be replaced by vendor.

- IG-55 control SYSTEM SKETCH

The attached sketch (Appendix 1) represent only the principles of system functioning and IG-55 system equipment (alarms, warning, light panels, etc.) location.

- IG-55 DEMAND CALCULATION

The number of cylinders is specified as Appendix 2.

APPENDIX 1

APPENDIX 2

.