## 1231 TQ Sheet
Remarks: 1- This TQ sheet shall be exchanged between PIDEC and Bidders in a native file. 2- Each column and cell shall be filled out just by concerning party means Bidders and PIDEC. 3- A telephone conversation may be held to close outstanding issues after 2 times exchanging of comments and clarification. 4- Please care that all cell to be formatted in Wrap Text setting and do not try to change column width.
EPs Contractor: |  |  | ZANJAN UREA FERTILIZER PROJECT |  |  |  | Owner:
Petrochemical Industries Design & Engineering Company (PIDEC)
TQ No.:
Project No. : 1231 |  |  | REQ No.: | 1231-DE-10-RE-REQ-330 |  | Rev.: | Project No. : 214
E.INSTRUMENT
E.1 |  | Following Documents shall be followed by vendor for design and supplying of Control & Safety system of Package : Doc. No. : 1231-DE-00-IN-MSS-673-01 Doc. No.: 1231-DE-00-IN-MSS-602-01 (for safety loops which shall be specified based on result of HAZOP and SIL study) Doc. No. : 1231-DE-00-IN-MSS-672-02 As specification of Control & Safety system has not been cleared in Technical Offer clearly ,and there is no vendor confirmation to show that above mentioned Documents will be followed by him for design and supplying of Control & Safety system ,it is expected that any deviation to be judged and advised or confirmed by Owner. |  |  | First of all, we agreed with Owner that reference of project execution will be agreed offer and technical clarification and comments discussed and agreed. Doc. No. : 1231-DE-00-IN-MSS-672-02 is NOT available in the requisition and therefore, it is NOT considered. Comments to Doc. No. : 1231-DE-00-IN-MSS-673-01 are listed below: * Vendor equipment includes power supply, communication modules of PLC to be redundant and no further reduandancy is agreed. Also, offer does NOT include any redundant I/Os same as our design in SABIC, ARAMCO, etc. Only we have ESD push bottom and remote trip signal from client ESD which are wired to separate IO cards.. * Due to the type of equipment, DELTA offer includes 10% spare on the hardware, and 20% spares of the memory. As specified in agreed offer, Instrumenation and Control will be as per MYCOM STD in Oil and Gas Area. * 2oo3 voting is not included.
Comments to Doc.1231-DE-00-IN-MSS-602-01 (for safety loops which shall be specified based on result of HAZOP and SIL study) are listed below: * vendor offer includes Vendor equipment includes power supply, communication modules of PLC to be redundant and no further reduandancy is agreed., but does NOT include any redundant I/Os for control nor ESD to protect the system to meet the requirements listed in this specification. * Offered equipment does NOT include a dedicated ESD system as DELTA will include special STOP and SHUTDOWN sequences to protect the equipment. This deisgn has been used on all off-shore and on-shore equipement for safe operations. * ESD push bottom and remote trip signal from client ESD are wired to separate IO cards.
E.2 |  | Following Documents shall be followed by vendor for instruments selection/supplying and design and supplying of Control & Safety system : Doc. No. : 1231-DE-00-IN-ESS-603-01 Doc. No.: 1231-DE-10-RE-REQ-330 (section 3.18 (INSTRUMENTATION)) As specification of Control & Safety system and instruments have not been cleared in Technical Offer clearly ,and there is no vendor confirmation to show that above mentioned Documents will be followed by him for design and supplying of Control & Safety system and selection/supplying instrument ,it is expected that any deviation to be judged and advised or confirmed by Owner. |  |  | For Doc. No. : 1231-DE-00-IN-ESS-603-01, DELTA design does not allow any auto start for the 2nd compressor. The 2nd compressor shall be brought into operation manually and have both compressor load sharing. Detailed procedure will be provided during detailed engineering. Instrument located on the local control station will be hermetically sealed to meet the area class, and the JB will be Ex(ec). Locally mounted solenoid valves will be rated for Ex(de), and all transmitters will be rated for Ex(ia). Instrument taps on the compressor packages will be per manufacturer standard as shown on offered P&ID. Offered pressurel gauges are 4.5". Offered Temperature gauges are 5". Due to space limitation, thermowell installation on the compressor packages are per manufacturer standard based on their common standards based many years of experience. Offered panel is per Type C.
Wire colors inside the package including remotely mounted panel are per manufacturer standar due to 1) the quantity of cable used on the system is extremely small, 2) availaibility in the market in small quantities. Tubing in the compressor package is manufscturer standard and may be less than 1/2". All instruments will include only main isolation valves to isolate them during service. Instrument installation and supports are per manufacturer standards.
For Doc. No.: 1231-DE-10-RE-REQ-330 (section 3.18 (INSTRUMENTATION)) see below comments. * SIL Study is normally covered by a 3rd party and not vendor. * Machine Monitoring Vibration equipments are not offered due to the size of the equipment and not required. * Due to the type of equipment, Vendor offer includes 10% spare on the hardware, and 20% spares of the memory. * 2oo3 voting is not included. * Vendor equipment includes power supply, communication modules of PLC to be redundant and no further reduandancy is agreed.
|  | It is expected that items E.3 ~ E.39 to be followed by Vendor so in case of any deviation ,it should be judged and advised or confirmed by Owner. |  |  | Refer to below reply.
E.3 |  | Original software and operating systems with all required licenses (Soft key or Hard key) shall be provided for Engineering Laptop and A copy of all original software with their licenses and also a copy of database of package software on compact disk (CD or DVD) shall be deliver to owner separately. |  |  | Operation software will be provided, configuation software is property of Vendor. DELL/ Lenovo Brand Cori5 laptop will be provided/
E.4 |  | Since the control cabinets will be installed in control room ,minimum IP42 is required for the cabinets. |  |  | Confirmed
E.5 |  | Field instruments shall be smart instruments with 4~20 mA signal and HART protocol. |  |  | Confirmed
E.6 |  | Electronic transmitters in hazardous area shall be basically intrinsic safe. Solenoid valves shall be Exia. |  |  | Confirmed for transmitters, however, solenoid valves, hand switches, push button, and pilot lights are Ex(d)
E.7 |  | All limit switches for automatic valves shall be proximity (NUMOR) type and intrinsically safe. |  |  | Housing for compressor slide valve assembly that includes limit switches and potentiometers is indeed Ex(ia) but requires barriers *current convertor) located inside the panel.
E.8 |  | Solenoid valves shall be IS with 24 VDC voltage rating. The material of body and trim to be SS 316. Coil housing material to be metalic not plastic. It should be noted that : - The distance between PU-5001 (Refrigeration Package) in Field and Package PLC and its marshalling cabinet in auxiliary room is approximately 260 meters. - The multi cable type which will be used for solenoid valves is 10x(2x1.5)+SCR. |  |  | Confirmed
E.9 |  | All transmitters shall be provided with integral digital indicators. |  |  | Confirmed
E.10 |  | Isolating valves shall be provided for all instruments. Two valve manifold for pressure switches and gauges and 5-valve manifold for DP transmitters shall be considered. |  |  | All trasnmitter will be located locally and only route valves will be used for isolation and mani fold is not required.
E.11 |  | All cable entries shall be M20X1.5 with explosion-proof cable glands. It shall be suitable for armored cable. |  |  | Confirmed
E.12 |  | The instrumentation shall be rated to withstand the environmental conditions specified in the engineering standard specification for ambient and site condition. |  |  | Confirmed
E.13 |  | All instrument/automatic valves wetted parts and process/air tubing materials shall be S.S. 316 as minimum, other materials as per process conditions. |  |  | Tubings will be SS 316
E.14 |  | Where ever temperature shall be transmitted to the package PLC, temperature transmitter shall be provided by vendor. Direct connection of temperature element to PLC is not acceptable. |  |  | Confirmed with the following clarifications: * Winding RTD are wired directly to MCC(if MV motor) * Compressor bearing RTDs are not required and agreed. * Motor bearing RTDs are not provided since the motor is ant-friction ball bearing
E.15 |  | Emergency shutdown sensors shall not be common with those of control loops. |  |  | Confirmed as for fail safe system, ESD butoon is a hard wire and normally wired to kill all outputs from PLC.
E.16 |  | All field instruments shall be factory calibrated with calibration certificate. |  |  | Confirmed
E.17 |  | In addition to isolation valve, dedicated manifold shall be considered and provided by vendor in each instrument hook up (for pressure & diff. pressure instruments). |  |  | All trasnmitter will be located locally and only route valves will be used for isolation and mani fold is not required.
E.18 |  | For off-skid loose and skid mounted instruments, all related Single Cables (40 meter for each item), Cable Glands, open conduits, pipe, tube (in SS316), fittings (in SS316), isolation and drain valves, manifolds, junction boxes, cable trays, instrument support, etc. shall be supplied by vendor based on Process & air Instrument Hook-ups and Instrument Field layout which shall be supplied by him. |  |  | Confirmed and all installation drawing will be shared during design review
E.19 |  | Skid & off-skid loose instruments and JB locations and cable routing shall be shown on Instrument Field layout. |  |  | Vendor confirms the following in the 3D model: * Cable trays routing * Instrument hookup with tube routing * Instrument location
E.20 |  | All panels, enclosures and junction boxes shall be explosion protected according to their area classification. All field mounted instruments, enclosures and junction boxes shall be protected to IP-65. |  |  | Confirmed for skid mounted instruments and junction boxes
E.21 |  | Terminals No. in Package PLC cabinets shall be mirror of terminals in junction boxes/interposing cabinet. |  |  | Confirmed
E.22 |  | All plant cables shall be fire retardant. |  |  | Confirmed per IEC 331 and IEC 332
E.23 |  | The available power supply in the control room is 110 V AC, 50 Hz UPS (redundant feeders in control room). Any requirement to another level of voltage , are in vendor scope of supply. Any distribution for 110VAC/UPS inside the package battery limit, are in vendor scope of supply as well. Also one 230VAC, non UPS will be made available by purchaser for Internal lamps and socket outlets in PLC cabinets of package. |  |  | Confirmed and noted
E.24 |  | Page 6 of 16 of Doc. No.:1231-DE-00-IN-SKT-007 shall be followed by vendor for Instrument/Electrical Connection Details as a typical sketch for signals which are applicable for vendor's electrical motors. Signals from/to MCC’s shall be considered as non-IS and hardwire type. All digital inputs/outputs from/to MCC shall be relay type (relays must be in vendor cabinet and shall be powered from vendor cabinet (output contact from these relays shall be wet and powered by 24Vdc inside PLC)). |  |  | Noted.
E.25 |  | TAG No. of each terminal strip in Package PLC cabinets shall be same as MULTICORES No. which will be specified by purchaser. |  |  | Confirmed
E.26 |  | IS and NIS signals shall be separated inside panels. (Two rout cables shall be considered). As per IEC-60332-1/BS-5308, IS cables shall be blue and NIS cables shall be gray. |  |  | Confirmed
E.27 |  | Separate IE/PE earth bar shall be considered inside the panels. |  |  | Confirmed
E.28 |  | Redundant DI & DO signals shall be foreseen by vendor for communication with plant hardwire console (Supplied by others). HS-50301 (Emergency Stop Signal; Trip PU-5001)(NIS,REDUNDANT,PASSIVE,24 VDC / POTENTIAL FREE CONTACT) HL-50301 (Common shutdown alarm from package PLC (UCP) to Plant HWC)(NIS,REDUNDANT,PASSIVE,24 VDC (CONSUMER LOAD)) |  |  | Vendor does offer redunadant DI & DO for the following reasons: * Vendor equipment includes power supply, communication modules of PLC to be redundant and no further reduandancy is agreed.s, but does NOT include any redundant I/Os. * Offered equipment does NOT include a dedicated ESD system as Vendor will include squential STOP and SHUTDOWN sequences to protect the equipment. This deisgn has been used on all off-shore and on-shore equipement for safe operations. * ESD push bottom and remote trip signal from client ESD are wired to separate IO cards.. * System will detect a bad PV anytime trip devices are failing. All hardwired signal for ESD will be wired to two different DI card to assure redundancy. DELTA offer requires all signal in dry state.
E.29 |  | The required shut-down, start-up and inter-lock diagrams based on IEC 61131 shall be provided and implemented in packages PLC’s by Vendor. |  |  | Vendor standard documents will be provided for the following: * Setpoint List * C&E * IO List * ¦Control Narrative + Startup, Stop, and ESD Sequences.
E.30 |  | The system logic shall be ‘fail safe’. All instruments shall be considered for fail to safe action upon loss of instrument air or electrical power. The input contacts to alarm, interlock and emergency shutdown system shall be close (make contact) during normal operation and open on alarm or trip. The solenoids shall be energized during normal operation and de-energized to trip. |  |  | Confirmed
E.31 |  | The PLC’s shall be provided with all required system software including application/utility programs, engineering/configuration tools, self-checking and selfdiagnostic fault detection capabilities. |  |  | Operation software will be provided, configuation software is property of Vendor. DELL/ Lenovo Brand Cori5 laptop will be provided/
E.32 |  | Vendor shall supply any required software/hardware for configuration of the PLC. The required soft-wares shall be installed on the laptop. The original software/dungle shall be included. |  |  | Operation software will be provided, configuation software is property of Vendor. DELL/ Lenovo Brand Cori5 laptop will be provided/
E.33 |  | All instrument items which are in vendor scope of supply and will be supplied as loose items by vendor shall be packed in separate box and marked properly "for instrumentation" during packing and shipment stage. |  |  | Confirmed
E.34 |  | The HAZOP and SIL study for package PIDs (vendor scope of work and supply) shall be performed by Vendor through third party. The Vendor quotation shall include all costs of performing HAZOP and SIL Studies for package PIDs including meetings, moderator, documentation, etc. The study results including HAZOP reports, HAZOP action close out sheets, SIL assessment and verification reports shall be submitted by vendor or study moderator as package vendor documents. The HAZOP study shall be performed according to IEC 61882 requirements. The SIL assessment/verification shall be performed according to IEC 61508 and IEC 61511 requirements. Since the Vendor is responsible for safety of package, all mandatory recommendations of HAZOP/SIL studies shall be incorporated without additional cost. |  |  | HAZOP and SIL studies are normally covered by contractor and NOT vendors. We will participate in client meeting with third party
E.35 |  | All the system hardware (including monitoring, control, protection, communications, communication with DCS, etc.) complete with all software (including application software) installed and loaded on the corresponding hardware, are subject to Factory Acceptance Test (FAT). FAT procedure shall be prepared by Vendor, approved by Owner and used as the guideline for performing FAT. Owner reserves the right to modify Vendor’s standard procedure. |  |  | Confirmed
E.36 |  | When Factory Acceptance Test (FAT) is over, the following features shall be available for future expansion: • a minimum of 20% installed spare breakers/fuses, • a minimum of 20% installed spare cores/pairs/triples terminals, • a minimum of 20% installed input/output spare points, • a minimum of 20% free space in cabinets, • 50% spare capacity for communication buses • 50% spare capacity for memory • 30% spare capacity for power supplies • 40% spare capacity for process controller unit |  |  | Refer to 1st item reply, these high requirement are not needed and nor agreed with Owner
E.37 |  | Commissioning and two years spare parts for instruments shall be quoted. Two years spare parts shall be according to Att. No. : 4 of Doc. No.: 1231-DE-10-RE-REQ-330 (Specific List of Spare Parts). |  |  | As per list provided by Owner
E.38 |  | Vendor's proposals shall cover the training according to section 12.6 of Doc. No.: 1231-DE-00-IN-MSS-673 (as an option). |  |  | As per agreement with Owner
E.39 |  | As most of Inst. Dept. technical documents were not found in submitted VPIS ,VPIS should be modified according to comments marked in green color. Vendor documentation shall be in PROJECT format. |  |  | Please find our replies