| Inspection & Test Plan (ITP) for Refrigeration Unit (PK-6101) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PURCHASER'S COMMENT/APPROVAL STATUS |  |  |  |  | Purchaser: NARGAN |  |  |
| 1. | AP: Approved (Released for Manufacturing) |  |  |  |  |  |  |
| 2. | AN: Approved With Minor Comments (Fabrication may Proceed) |  |  |  | Requisition No.: DPIC98-12-001-000-ME-MR- 4150-0001-D1 |  |  |
| 3. | NF: Approved With Comments (Fabrication not Proceed) |  |  |  |  |  |  |
| 4. | RJ: Rejected |  |  |  | Item No. (Tag No.): PK-6101 |  |  |
| 5. | NR: Not be Returned |  |  |  |  |  |  |
| Date: XX.XX.XX Signature: |  |  |  |  | Vendor Doc. No.: DPIC9812-000-VD-1002-ME-ITP-0008 |  |  |
| D1 |  | 04-Jan-2022 | Issue for Approval | M. R | M. M | A.V |  |
| D0 |  | 16-Nov-2021 | Issue for Approval | M. R | M. M | A.V |  |
| REV. |  | DATE ISSUE | Purpose of Issue | PREPARED | CHECKED | APPROVED |  |

TABULATION OF REVISED PAGES

| Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4 |  | Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4 |  | Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | x |  |  |  |  |  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | x |  |  |  |  |  | 26 |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | x | x |  |  |  |  | 27 |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | x | x |  |  |  |  | 28 |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | x | x |  |  |  |  | 29 |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | x | x |  |  |  |  | 30 |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | x | x |  |  |  |  | 31 |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | x | x |  |  |  |  | 32 |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | x | x |  |  |  |  | 33 |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | x | x |  |  |  |  | 34 |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | x | x |  |  |  |  | 35 |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 | x | x |  |  |  |  | 36 |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 | x | x |  |  |  |  | 37 |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 38 |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 39 |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 40 |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 41 |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 42 |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 43 |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 44 |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 45 |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 46 |  |  |  |  |  |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 47 |  |  |  |  |  |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 48 |  |  |  |  |  |  |  |  |  |  |  |  |

| SIGN: ASME VIII DIV. 1 |  | ITEM NO(S).: DEJDASHT PETROCHEMICAL Refrigeration Package |  |  |  |  |  | MANUFACTURER SERIAL NUMBER: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Scope | This Inspection and Test plan covers all activities that will be carried out in design and fabrication of equipment. |  |  |  |  |  |  |  |  |  |  |  | Date: |
| 2 | LEGEND OF THE TECHNICAL SURVEILLANCE | - (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next fabrication stage is subject to acceptance of inspection. Vendor must notify parties activity) of the defecated inspection activity at least fifteen (15) days in advance. |  |  |  |  |  |  |  |  |  |  |  | Rev.: D0 |
|  |  | - (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces. |  |  |  |  |  |  |  |  |  |  |  | By: |
|  |  | - (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test. |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order. |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - (M) = KASRAVAND(Manufacturer) Inspection |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Abbreviations | O = Owner (Dehdasht PC/PIDMCO) N = NARGAN V = Vendor SV = Sub Vendor TPI = Third Party Inspection on behalf of owner |  |  |  |  |  |  |  |  |  |  |  |  |
| Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria |  |  | INSPECTION ACTIVITY |  |  |  |  |  | REMARKS |  |
|  |  |  |  |  |  |  | SV |  | V | N | TPI | O/MC |  |  |
| A PROJECT PREPARATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A1 | VERIFY CUSTOMER SPECIFICATION | ASME VIII DIV 1 (U-STAMP NOT REQUIRED)(Welding Standard) DETAILS AS PER QUALITY PLAN |  |  |  | Type | H |  | H |  |  |  |  |  |
|  |  |  |  |  |  | Date |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Sign |  |  |  |  |  |  |  |  |
| A2 | PRE INSPECTION MEETING |  | MOM & ITP |  |  | Type | H |  | H | H |  | H |  |  |
|  |  |  |  |  |  | Date |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Sign |  |  |  |  |  |  |  |  |

| Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria |  |  |  | INSPECTION ACTIVITY |  |  |  |  | REMARKS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | SV | V | N | TPI | O/MC |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |
| B MATERIAL SELECTION / SUBCONTRACTOR ORDERING |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B0 | GENERAL | ALL ITEMS SUITABLE FOR AMBIENT TEMPERATURE / OUTDOOR ALL ITEMS TO BE CONFORM ZONE 2 GROUP IIB T3 | MATERIAL SUPPLY FABRICATION SCHEDULE QA / QC |  |  |  | Type | H | H |  |  |  |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |
| B1 | COMPRESSOR –SUBCONTRACTED MAYEKAWA FACTORY JAPAN | DETAILS AS PER COMPRESSOR QUALITY PLAN MANUFACTURER STANDARD | TEST REPORT: -Noise test. - Vibration test - Performance test - Running test - Hydro test |  | MATERIAL CERTIFICATES |  | Type | See ITP of Compressor |  |  |  |  |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |
| B2 | MAIN MOTOR - SUBCONTRACTED | Refer to MOTOR ITP | TEST REPORT - Unwitnessed routine test report |  |  |  | Type | See ITP of MV Motor |  |  |  |  |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |
| B3 | OIL PUMP MAYEKAWA FACTORY | MYCOM STANDARD | TEST REPORT incl; Hydro test result and performance test result |  | MATERIAL CERTIFICATES |  | Type | H | H | R | R |  |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |
| B4 | PUMP MOTOR | MANUFACTURER STANDARD with protection class as per Exn HAZARDOUS AREA CERTIFICATEI IECex / Exn Zone 2 IIB T3 | TEST REPORT ( Manuf. Std ) - Unwitnessed routine test report |  |  |  | Type | H | H | R | R |  |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |
| B5 | MAIN COUPLING | MYCOM STANDARD (Flexible disc type coupling ) | SUITABLE FOR HAZARDOUS AREA |  | Material certificate, visual and dimensional inspection report |  | Type | H | H | R | R |  |  |
|  |  |  |  |  |  |  | Date |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Sign |  |  |  |  |  |  |

| B6 | PRESSURE VESSELS Double Oil filter (with element)Oil separator (with coalescer) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| B6-1 | Material Inspection & Certificate review (Pressure Part) | App DWG Project Documents, Material Standards | Material Certificate / Inspection report 2.2 Certificate for non-pressure Parts | Approved drawings. EN 10204‐3.1 Project Documents, Material Standards |  |  |  | H | H |  | W |  | W | R |  |
| B6-2 | Visual and dimensional check of fabricated heads | App. DWG | Head Dim. Report | Drawing Welding Map |  |  |  | H | H |  | W |  | W | R |  |
| B6-3 | Fit‐up and welding of shells and heads | WPS/PQR, WELD MAP | Inspection Report | ASME SEC VIII,IX, Project job specification |  |  |  | H | H |  | SW |  | SW | R |  |
| B6-4 | Marking of nozzles on heads prior to cutting | App. DWG | Inspection Report | Drawing |  |  |  | H | H |  | W |  | W | R |  |
| B6-5 | Fit‐up and welding of nozzles to heads | App. DWG | Inspection Report | Drawing |  |  |  | H | H |  | SW |  | SW | R |  |
| B6-6 | PWHT (if any) | Procedure | Inspection Report | Procedure |  |  |  | H | H |  | SW |  | SW | R |  |
| B6-7 | PMI test (if any) | Procedure | Inspection Report | Procedure |  |  |  | H | H |  | SW |  | SW | R |  |
| B6-8 | NDT | Procedure + NDT Map | Inspection Report | Procedure + NDT Map |  |  |  | H | H |  | RA |  | R | R | 100% RTI & 20% W for Other NDT |
| B6-9 | Final Visual & Dimensional Check | App DWG/ ASME Sec VIII,IX | Inspection Report | App DWG/ ASME Sec VIII,IX |  |  |  | H | H |  | W |  | W | R |  |
| B6-10 | Hydrostatic and Leak Test | Hydrostatic test procedure | Inspection Report | Hydrostatic test procedure |  |  |  | H | H |  | H |  | H | R |  |
| B6-11 | Final Painting Inspection | App. Painting Procedure Painting project specification | Inspection Report | App. Painting Procedure Painting project specification |  |  |  | H | H |  | H |  | H | R |  |
| B7 | HEAT EXCHANGERS CONDENSOR ECONOMIZER OIL COOLER EVAPORATOR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B7-1 | Material Inspection & Certificate review (Pressure Part) | App DWG Project Documents, Material Standards | Material Certificate / Inspection report 2.2 Certificate for non-pressure Parts | Approved drawings. EN 10204‐3.1 Project Documents, Material Standards |  |  |  | H | H |  | W |  | W | R |  |
| B7-2 | Visual and dimensional check of fabricated heads | App. DWG | Head Dim. Report | Drawing Welding Map |  |  |  | H | H |  | W |  | W | R |  |
| B7-3 | Fit‐up and welding of shells and heads | WPS/PQR, WELD MAP | Inspection Report | ASME SEC VIII,IX, Project job specification |  |  |  | H | H |  | SW | SW |  | R |  |
| B7-4 | Marking of nozzles on heads prior to cutting | App. DWG | Inspection Report | Drawing |  |  |  | H | H |  | W | W |  | R |  |
| B7-5 | PWHT (if any) | Procedure | Inspection Report | Procedure |  |  |  | H | H |  | SW | SW |  | R |  |
| B7-6 | PMI test (if any) | Procedure | Inspection Report | Procedure |  |  |  | H | H |  | SW | SW |  | R |  |
| B7-7 | Fit‐up and welding of nozzles to heads | App. DWG | Inspection Report | Drawing |  |  |  | H | H |  | SW | SW |  | R |  |
| B7-8 | NDT | Procedure + NDT Map | Inspection Report | Procedure + NDT Map |  |  |  | H | H |  | RA | R |  | R | 100% RTI & 20% W for Other NDT |
| B7-9 | Final Visual & Dimensional Check | App DWG/ ASME Sec VIII,IX | Inspection Report | App DWG/ ASME Sec VIII,IX |  | Type |  | H | H |  | W | W |  | R |  |
| B7-10 | Hydrostatic and Leak Test | Hydrostatic test procedure | Inspection Report | Hydrostatic test procedure |  | Type |  | H | H |  | H | H |  | R |  |
| B7-11 | Final Painting Inspection | App. Painting Procedure Painting project specification | Inspection Report | App. Painting Procedure Painting project specification |  | Type |  | H | H |  | H | H |  | R |  |
| B8 | BASE FRAME |  | PT -10 % OF MAJOR STRUCTURAL CONNECTIONS 100 % PT LIFTING LUG WELDS VT and DT | ACC. DATASHEET/ DRAWING SKID CONNECTION POINTS ANCHOR BOLT POSITIONS INSPECTION /2.2 CERTIFICATE, AWS D1.1 |  | Type |  | H | H |  | W | W |  | R |  |
| B9 | VALVES |  | MATERIAL CERTIFICATES 3.1 FOR MAJOR PARTS MANUFACTURER INSPECTION AND TEST RECORD HYDROSTATIC REPORT , VT and DT | ACC. DATASHEET/ DRAWING INSPECTION /CERTIFICATE |  | Type |  | H | H |  | SW | SW |  | R |  |
| B10 | PIPING |  | 1. Carbon oil and refrigerant piping 10%. 2. SS Oil and refrigerant piping 10%. 3. Instrument air header 10%. Amount will be based on total amount of welded inches. VT and DT and welding visual check and PMI 100% of Process Piping will be Hydrostatic Tested in Presence of inspector | Material certificates |  | Type |  | H | H |  | W | W |  | R | 100% RTI & 20% W for Other NDT |
| B11 | SAFETY VALVES | ASME VIII DIV 1 without U-Stamp | MATERIAL CERTIFICATES 3.1 SET POINT CERTIFICATE CALCULATIONS TEST REPORT | Material certificates |  | Type |  | H | H |  | W | W |  | R |  |
| B12 | Smaller components within instrumentation routing, such AS TUBING and GASKETS and bolting. |  | MATERIAL CERTIFICATES 3.1 | Material certificates |  | Type |  | H | H |  | SW | SW |  | R |  |
| B13 | INSTRUMENTATION | MANUFACTURER STANDARD (Pressure and temperature gauges are provided with 2.2 material certificates) | MATERIAL CERTIFICATES 3.1 (Manifolds are provided with 3.1 Material certificates) DIMENSIONAL AND CONSTRUCTION DWG HAZARDOUS AREA CERTIFICATE CALIBRATION REPORT (3.1 material certificates). 3 point calibration |  |  | Type |  | H | H |  | W | W |  | R |  |
| B14 | PLC | MANUFACTURER STANDARD: 1.Software Redundancy 2.Redundancy required for CPU, power supply, communication card 3. Solenoid and On/Off valves will be executed in Exd. 4.Approved project document | BOM, Panel DWG, wiring DWG SAFE AREA project document Number: DPIC9812-000-VD-1002-ME-DIA-0040 |  |  | Type |  | H | H |  | W | W |  | R |  |
| B15 | Local control Panel | LCS Wiring and Drawing | Documents Number: DPIC9812-000-VD-1002-ME-DWG-0027 |  |  |  |  | H | H |  | W | W |  | R |  |
| B16 | ELECTRICAL ITEMS | LCS Wiring and Drawing | HAZARDOUS AREA CERTIFICATE Zone 2, IIB T3 |  |  | Type |  | H | H |  | W | W |  | R |  |
| C INSPECTION DOCUMENTS, PIPING |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C1 | WELDING DOCUMENTS (WPS/PQR/WELDMAP) | ASME B31.3 | Report |  |  | Type |  | H | H |  | R | R |  | R |  |
| C2 | WELDER'S QUALIFICATION | ASME IX | Report |  |  | Type |  | H | H |  | R | R |  | R |  |
| C3 | NDE PROCEDURES (UT/RT/MT/PT/HT) | ASME IX | NDT Map |  |  | Type |  | H | H |  | R/A | R |  | R |  |
| C4 | NDT OPERATORS | ASME V | Certificates |  |  | Type |  | H | H |  | R | R |  | R |  |
| C5 | Hydrostatic test procedure | ASME B31.3 | Report | Hydrostatic Test Procedure |  | Type |  | H | H |  | R | R |  | R |  |
| C6 | SURFACE PREPARATION & PAINTING COATING PROCEDURE | OEM STANDARD / SUPPLIER PROCEDURES | Report | Vendor Specification |  | Type |  | H | H |  | R | R |  | R |  |
| D MATERIALS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| D1 | VISUAL EXAMINATION AND DIMENSIONAL CHECK OF MATERIALS THICKNESS VERIFICATION | ASME II SA20 / ASME II Part A & C | REPORT OF DIMENSIONAL INSPECTION REPORT | DIMENSIONS SURFACE CONDITION |  | Type |  | H | H |  | W | W |  | R |  |
| D2 | MATERIAL CERTIFICATION AND MARKING | ACC. TO PROJECT REQUIREMENTS ( REFER TO PROJECT PACKAGE DATASHEET ) | MATERIAL MAP | 3.1.CERTIFICATE (For pressurized parts) 2.2 CERTIFICATE (for Non-pressurized parts) |  | Type |  | H | H |  | R | R |  | R |  |
| D3 | WELDING CONSUMABLES | MANUFACTURER STANDARD | 3.1 MATERIAL CERTIFICATE | ASME Sec. II, part C |  | Type |  | H | H |  | W | W |  | R |  |
| D4 | NON PRESSURE RETAINING PARTS | ASMEVIIIDIV1 (U-STAMP NOT REQUIRED ) | 2.2 MATERIAL CERTIFICATE (No PMI requirement for Valves/internals and equipment) | MANUFACTURING STANDARD |  | Type |  | H | H |  | R | R |  | R |  |
| D5 | BOLTING MATERIAL | As per relevant drawings | 3.1 MATERIAL CERTIFICATE | Certificate |  | Type |  | H | H |  | W | W |  | R |  |
| E INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| E1 | DIMENSIONAL INSPECTION OF SKID CONNECTION POINTS | drawings | SKID CONNECTION POINTS – ANCHOR BOLT POSITIONS | WITHIN TOLERANCE REPORT / AS BUILT DRAWING |  | Type |  | H | H |  | W | W |  | R |  |
| E2 | PARTS AND COMPONENT INSPECTION | MAYEKAWA STANDARD | P&ID COMPONENT (ORDER) LIST |  |  | Type |  | H | H |  | W | W |  | R |  |
| E3 | Air Leak Test of Whole Package | Relevant Procedure | PRESS REPORT ME-F-7.6.0-01-SO72522- Leak test report | MANUFACTURING STANDARD |  | Type |  | H | H |  | R | R |  | R |  |
| E4 | PMI Test (Welds) | According to Weld Map-NDT Map (If Applicable) | Report | ASME Sec II Part A & C |  | Type |  | H | H |  | W | W |  | R |  |
| E5 | PAINTING | OEM STANDARD/SUPPLIER_(Painting Standard) PAINT SPECIFICATION | THICKNESS VISUAL INSPECTION and measurement via instrument. PAINT INSPECTION REPORT | ACC SPECIFICATION |  | Type |  | H | H |  | W | W |  | R |  |
| E6 | ELECTRICAL WIRING | WIRING CHECK |  |  |  | Type |  | M | W |  | W | W |  | R |  |
| E7 | INSPECTION OF junction BOX, LOCAL PANEL AND PLC | FACTORY ACCEPTANCE TEST 1.VISUAL INSPECTION JUNCTION BOX, LOCAL PANEL AND PLC 2. CONTINUITY, POWER UP & WET LOOP CHECK 3. FUNCTION TEST (REDUNDANCY, LOGIC) | TEST REPORT FAT TEST PROCEDURE | LOGIC DIAGRAM CONTROL NARRATIVE DRAWINGS, DATA SHEETS |  | Type |  | M | H |  | H | H |  | R |  |
| E8 | FINAL INSPECTION | Vendor STANDARD | NAME PLATES CONFIRMATION | RELEASE NOTE |  | Type |  | M | H |  | H | H |  | R |  |
| F Spare Part |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| F1 | Material Inspection & Certificate review | App. Spare Part List | Material Certificate / Inspection report | EN 10204‐3.1 Project Documents, Material Standards |  |  |  | H | H |  | W | W |  | R |  |
| G SHIPMENT AND LOADING |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G1 | PACKING AND MARKING PREPARATION FOR SHIPMENT DETAILED PACKING LIST AND LOOSE DELIVERY LIST | Packing Procedure | PACKING INSPECTION VISUAL INSPECTION COMPLETENESS CHECK | PACKING LIST |  | Type |  | H | H | H |  | H |  | R |  |
| G2 | Inspection of preservation check | - | Report | VENDOR STANDARD |  |  |  | H | H | W |  | W |  | R |  |
| G3 | Manufacturer compliance certificate | - | MCC | - |  |  |  | H | R | R |  | - |  | R |  |
| G4 | Issue of shipping release note | - | SRN | - |  |  |  | R | R | R |  | H |  | R |  |
| F5 | Vendor data book | Final data book, ITP, etc. | A COMPLETE PACKAGE OF INSPECTION AND TEST RECORD/CERTIFICATE MANUFACTURED RECORD | VDB index list |  | Type |  | H | H | R/A |  | R |  | R |  |