## Cover Sheet
This document is the property of DPIC. Any unauthorized attempt to reproduce it, in any form, is strictly prohibited. |  |  |  | DEHDASHT PETROCHEMICAL INDUSTRY COMPANY DEHDASHT HIGH DENSITY POLYETHYLENE PROJECT
|  |  |  | DOCUMENT TITLE: Instrument Index List |  |  | POI: IFA | Rev.: D1
| Contract No.: DPIC/98-12 |  |  | DOCUMENT NUMBER: DPIC9812-000-VD-1002-ME-LST-0051 |  |  | Sheet 1 of 5
DOCUMENT TITLE:
Instrument Index List
| PURCHASER'S COMMENT/APPROVAL STATUS |  |  |  |  | Purchaser: NARGAN
| 1 | AP: Approved (Released for Manufacturing) |  |  |  | Requisition No.: DPIC98-12-001-000-ME-MR-4150-0001-D1
| 2 | AN: Approved With Minor Comments (Fabrication may Proceed) | 2. AN: Approved as Noted for Fabrication (Fabrication may Proceed)
| 3 | NF: Approved With Comments (Fabrication not Proceed) |  |  |  | Item No. (Tag No.): PK-6101
| 4 | RJ: Rejected
| 5 | NR: Not be Returned |  |  |  | Vendor Doc. No.: DPIC9812-000-VD-1002-ME-LST-0051
Date: XX.XX.XX Signature:
| D1 | 12.Feb..22 | R.Sabbaghi | A.MALEKINIA | DR.A.Nejati
| D0 | 05.Jan.22 | N.Heidaran | DR.A.Nejati | DR.A.Nejati
| REV | DATE ISSUE | PREPARED | CHECKED | APPROVED

## Revision Index
This document is the property of DPIC. Any unauthorized attempt to reproduce it, in any form, is strictly prohibited. |  |  |  | DEHDASHT PETROCHEMICAL INDUSTRY COMPANY DEHDASHT HIGH DENSITY POLYETHYLENE PROJECT
|  |  |  | DOCUMENT TITLE: Instrument Index List | [7 empty] | POI: IFA |  | Rev.: D1
| Contract No.: DPIC/98-12 |  |  | DOCUMENT NUMBER: DPIC9812-000-VD-1002-ME-LST-0051 | [7 empty] | Sheet 2 of 5
|  | Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4 | Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4
|  | 1 | x | x |  |  |  | 36
|  | 2 | x | x |  |  |  | 37
|  | 3 | x | x |  |  |  | 38
|  | 4 | x | x |  |  |  | 39
|  | 5 | x | x |  |  |  | 40
|  | 6 | [5 empty] | 41
|  | 7 | [5 empty] | 42
|  | 8 | [5 empty] | 43
|  | 9 | [5 empty] | 44
|  | 10 | [5 empty] | 45
|  | 11 | [5 empty] | 46
|  | 12 | [5 empty] | 47
|  | 13 | [5 empty] | 48
|  | 14 | [5 empty] | 49
|  | 15 | [5 empty] | 50
|  | 16 | [5 empty] | 51
|  | 17 | [5 empty] | 52
|  | 18 | [5 empty] | 53
|  | 19 | [5 empty] | 54
|  | 20 | [5 empty] | 55
|  | 21 | [5 empty] | 56
|  | 22 | [5 empty] | 57
|  | 23 | [5 empty] | 58
|  | 24 | [5 empty] | 59
|  | 25 | [5 empty] | 60
|  | 26 | [5 empty] | 61
|  | 27 | [5 empty] | 62
|  | 28 | [5 empty] | 63
|  | 29 | [5 empty] | 64
|  | 30 | [5 empty] | 65
|  | 31 | [5 empty] | 66
|  | 32 | [5 empty] | 67
|  | 33 | [5 empty] | 68
|  | 34 | [5 empty] | 69
|  | 35 | [5 empty] | 70

## NOTES AND ABBREVIATIONS
DEHDASHT PETROCHEMICAL INDUSTRY COMPANY DEHDASHT HIGH DENSITY POLYETHYLENE PROJECT
|  |  |  | DOCUMENT TITLE: Instrument Index List |  |  | POI: IFA | Rev.: D1
| Contract No.: DPIC/98-12 |  |  | DOCUMENT NUMBER: DPIC9812-000-VD-1002-ME-LST-0051 |  |  | Sheet 3 of 5
This document is the property of DPIC. Any unauthorized attempt to reproduce it, in any form, is strictly prohibited. |  | NOTES:
|  | 1. | Following instrument index covers Refrigeration Unit (PK-6101) of "Dehdasht Petrochemical Co. HDPE Project"
|  | 2 | All of the Signals are assumed to be shared with Central Plant Control System via Serial Communcation
ABBREVIATIONS:
|  | 1. |  | Input/Output:
|  |  |  | • | AI | : Analog Input
|  |  |  | • | AO | : Analog Output
|  |  |  | • | DI | : Digital Input |  |  | : Analog+E22:T31 Output
|  |  |  | • | DO | : Digital Output
|  |  |  | • | DIX | : Digital Input - SERIAL DATA
|  |  |  | • | DOX | : Digital Output - SERIAL DATA
|  |  |  | • | AIX | : Analog Input - SERIAL DATA
|  |  |  | • | AOX | : Analog Output - SERIAL DATA
|  | 2. |  | Signal Types:
|  |  |  | • | H | : Hardwired
|  |  |  | • | C | : Communication
|  |  |  | • | I | : Internal Block
|  |  |  | • | P/N | : Pneumatic
|  | 3. |  | Location/System:
|  |  |  | • | F | : Field
|  |  |  | • | PCR | : Plant Control Room
|  |  |  | • | CCR | : Central Control Room
|  |  |  | • | S/S | : Substation
|  |  |  | • | MCC | : Motor Control Center
|  |  |  | • | 100UP-01 | : Package Main Panel (Located in Rack Room)
Page 3 of 5

## INSTRUMENT INDEX LIST
DEHDASHT PETROCHEMICAL INDUSTRY COMPANY DEHDASHT HIGH DENSITY POLYETHYLENE PROJECT
DOCUMENT TITLE: Instrument Index List
Contract No.: DPIC/98-12 |  |  | DOCUMENT NUMBER: DPIC9812-000-VD-1002-ME-LST-0051
Item No. | Instrument Tag Number | Instrument Type | Service | Signal | NS/NIS | Location | System | Signal Type | Signal Level | P&ID DPIC9812-000-VD-1002-ME-LST-0051 | Fluid | Measuring Unit | Range/Set Point | Line/Equipment No. | MODEL AND MFR (Note.01) | Remarks | Rev.
A | PRESSURE GAUGES
1 | PG-61120 | PRESSURE GAUGE (BOURDON TUBE) | LIQUID RECEIVER (D-PK6101-2) PROPYLENE INLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | -1~+30 | 8"-PR-61122-1DL4-M |  |  | D1
2 | PG-61124 | PRESSURE GAUGE (BOURDON TUBE) | EVAPORATOR (E-6101) PROPYLENE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | -1~+30 | 12"-PR-61136-1DL4-M |  |  | D1
3 | PG-61134 | PRESSURE GAUGE (BOURDON TUBE) | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 3/4 | PROPYLENE | BARG | -1~+30 | 8"-PR-61142-1DL4-P |  |  | D1
4 | PG-61138 | PRESSURE GAUGE (BOURDON TUBE) | OIL PUMP (P-PK6101-1A) DISCHARGE | N/A | N/A | FIELD | N/A | N/A | N/A | 3/4 | OIL | BARG | -1~+30 | 3"-OIL-61124-1DL4-E |  |  | D1
5 | PG-61139 | PRESSURE GAUGE (BOURDON TUBE) | OIL PUMP (P-PK6101-2A) DISCHARGE | N/A | N/A | FIELD | N/A | N/A | N/A | 3/4 | OIL | BARG | -1~+30 | 3"-OIL-61125-1DL4-E |  |  | D1
6 | PG-61149 | PRESSURE GAUGE (BOURDON TUBE) | SCREW COMPRESSOR (C-PK6101-1B ) PROPYLENE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 4/4 | PROPYLENE | BARG | -1~+30 | 8"-PR-61144-1DL4-P |  |  | D1
7 | PG-61153 | PRESSURE GAUGE (BOURDON TUBE) | OIL PUMP (P-PK6101-1B) DISCHARGE | N/A | N/A | FIELD | N/A | N/A | N/A | 4/4 | OIL | BARG | -1~+30 | 3"-OIL-61134-1DL4-E |  |  | D1
8 | PG-61154 | PRESSURE GAUGE (BOURDON TUBE) | OIL PUMP (P-PK6101-2B) DISCHARGE | N/A | N/A | FIELD | N/A | N/A | N/A | 4/4 | OIL | BARG | -1~+30 | 3"-OIL-61135-1DL4-E |  |  | D1
B | TEMPERATURE GUAGES
1 | TI-61120 | TEMPERATURE GAUGE | LIQUID RECEIVER (D-PK6101-2) | N/A | N/A | ON ELEMENT | N/A | N/A | N/A | 2/4 | N/A | ⁰C | 0~+100 | TE-61120 |  |  | D1
2 | TI-61121 | TEMPERATURE GAUGE | K.O DRUM (D-PK6101-3) | N/A | N/A | ON ELEMENT | N/A | N/A | N/A | 2/4 | N/A | ⁰C | -50~+50 | TE-61121 |  |  | D1
3 | TI-61124 | TEMPERATURE GAUGE | EVAPORATOR (E-6101) | N/A | N/A | ON ELEMENT | N/A | N/A | N/A | 2/4 | N/A | ⁰C | -50~+50 | TE-61124 |  |  | D1
4 | TI-61126 | TEMPERATURE GAUGE | EVAPORATOR (E-6101) COLD HEXANE TUBE OUTLET | N/A | N/A | ON ELEMENT | N/A | N/A | N/A | 2/4 | N/A | ⁰C | -50~+50 | TE-61126 |  |  | D1
5 | TI-61137 | TEMPERATURE GAUGE | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE OUTLET | N/A | N/A | ON ELEMENT | N/A | N/A | N/A | 2/4 | N/A | ⁰C | -50~+50 | TE-61137 |  |  | D1
6 | TI-61140 | TEMPERATURE GAUGE | EVAPORATOR (E-6101) COLD HEXANE TUBE INLET | N/A | N/A | ON ELEMENT | N/A | N/A | N/A | 2/4 | N/A | ⁰C | -50~+50 | TE-61140 |  |  | D1
C | PRESSURE TRANSMITTERS
1 | PT-61121 | PRESSURE TRANSMITTER | LIQUID RECEIVER (D-PK6101-2) | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | BARG | -1~+30 | D-PK6101-2 |  |  | D1
2 | PT-61122 | PRESSURE TRANSMITTER | ECONOMIZER (E-PK6101-3) PROPYLENE INLET TEMPERATURE CONTROL SETPOINT (CASCADE) | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | BARG | -1~+25 | 6"-PR-61127-1DL4-M |  |  | D1
3 | PT-61126 | PRESSURE TRANSMITTER | K.O DRUM (D-PK6101-3) PROPYLENE OUTLET PRESSURE MEASUREMENT & CONTROL | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | BARG | -1~+25 | 12"-PR-61140-1DL4-M |  |  | D1
4 | PT-61129 | PRESSURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-A) PROPYLENE INLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | PROPYLENE | BARG | -1~+25 | 12"-PR-61140-1DL4-M |  |  | D1
5 | PT-61131 | PRESSURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE OUTLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | PROPYLENE | BARG | -1~+25 | 8"-PR-61142-1DL4-P |  |  | D1
6 | PT-61135 | PRESSURE TRANSMITTER | OIL SEPARATOR (D-PK6101-1A) PROPYLENE OUTLET PRESSURE MEASUREMENT & CONTROL | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | PROPYLENE | BARG | 0~30 | D-PK6101-1A |  |  | D1
7 | PT-61137 | PRESSURE TRANSMITTER | OIL SEPARATOR (D-PK6101-1A) PROPYLENE OUTLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | PROPYLENE | BARG | -1~30 | 8"-PR-61120-1DL4-P |  |  | D1
8 | PT-61140 | PRESSURE TRANSMITTER | OIL FILTER (F-PK6101-1A/2A) OIL INLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | OIL | BARG | 0~30 | 3"-OIL-61124-1DS4-E |  |  | D1
9 | PT-61142 | PRESSURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-A) OIL INLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | OIL | BARG | 0~30 | 3"-OIL-61126-1DS4-E |  |  | D1
10 | PT-61144 | PRESSURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-B) PROPYLENE INLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | PROPYLENE | BARG | -1~+25 | 12"-PR-61141-1DL4-M |  |  | D1
11 | PT-61146 | PRESSURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE OUTLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | PROPYLENE | BARG | -1~+25 | 8"-PR-61144-1DL4-P |  |  | D1
12 | PT-61150 | PRESSURE TRANSMITTER | OIL SEPARATOR (D-PK6101-1B) | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | PROPYLENE | BARG | 0~30 | D-PK6101-1B |  |  | D1
13 | PT-61152 | PRESSURE TRANSMITTER | OIL SEPARATOR (D-PK6101-1B) PROPYLENE OUTLET PRESSURE MEASUREMENT & CONTROL | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | PROPYLENE | BARG | -1~30 | 8"-PR-61121-1DL4-P |  |  | D1
14 | PT-61155 | PRESSURE TRANSMITTER | OIL FILTER (F-PK6101-1B/2B) OIL INLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | OIL | BARG | 0~30 | 3"-OIL-61134-1DS4-E |  |  | D1
15 | PT-61157 | PRESSURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-B) OIL INLET | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | OIL | BARG | 0~30 | 3"-OIL-61136-1DS4-E |  |  | D1
D | THERMOWELL
1 | TW-61120 | THERMOWELL | LIQUID RECEIVER (D-PK6101-2) | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | D-PK6101-2 |  |  | D1
2 | TW-61121 | THERMOWELL | K.O DRUM (D-PK6101-3) | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | D-PK6101-3 |  |  | D1
3 | TW-61122 | THERMOWELL | ECONOMIZER (E-PK6101-3) PROPYLENE INLET TEMPERATURE MEASUREMENT & CONTROL | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 6"-PR-61127-1DL4-M |  |  | D1
4 | TW-61124 | THERMOWELL | EVAPORATOR (E-6101) | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 6"-PR-61127-1DL4-M |  |  | D1
5 | TW-61125 | THERMOWELL | EVAPORATOR (E-6101) COLD HEXANE TUBE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | COLD HEXANE | N/A | N/A | 20"-CHXS-61104-1DL1-M |  |  | D1
6 | TW-61126 | THERMOWELL | EVAPORATOR (E-6101) COLD HEXANE TUBE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | COLD HEXANE | N/A | N/A | 20"-CHXS-61104-1DL1-M |  |  | D1
7 | TW-61130 | THERMOWELL | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 3/4 | OIL | N/A | N/A | 8"-PR-61142-1DL4-P |  |  | D1
8 | TW-61132 | THERMOWELL | OIL FILTER (F-PK6101-1A/2A) OIL OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 3/4 | OIL | N/A | N/A | 3"-OIL-61126-1DS4-E |  |  | D1
9 | TW-61134 | THERMOWELL | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 4/4 | OIL | N/A | N/A | 8"-PR-61144-1DL4-P |  |  | D1
10 | TW-61137 | THERMOWELL | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 6"-PR-61127-1DL4-M |  |  | D1
11 | TW-61140 | THERMOWELL | EVAPORATOR (E-6101) COLD HEXANE TUBE INLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | COLD HEXANE | N/A | N/A | 18"-CHXR-61101-1DL1-M |  |  | D1
12 | TW-61141 | THERMOWELL | OIL FILTER (F-PK6101-1B/2B) OIL OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 4/4 | OIL | N/A | N/A | 3"-OIL-61136-1DS4-E |  |  | D1
E | TEMPERATURE ELEMENT
1 | TE-61120 | TEMPERATURE ELEMENT | LIQUID RECEIVER (D-PK6101-2) | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61120 |  |  | D1
2 | TE-61121 | TEMPERATURE ELEMENT | K.O DRUM (D-PK6101-3) | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61121 |  |  | D1
3 | TE-61122 | TEMPERATURE ELEMENT | ECONOMIZER (E-PK6101-3) PROPYLENE INLET TEMPERATURE MEASUREMENT & CONTROL | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61122 |  |  | D1
4 | TE-61124 | TEMPERATURE ELEMENT | EVAPORATOR (E-6101) | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61124 |  |  | D1
5 | TE-61125 | TEMPERATURE ELEMENT | EVAPORATOR (E-6101) COLD HEXANE TUBE OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61125 |  |  | D1
6 | TE-61126 | TEMPERATURE ELEMENT | EVAPORATOR (E-6101) COLD HEXANE TUBE OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61126 |  |  | D1
7 | TE-61130 | TEMPERATURE ELEMENT | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 3/4 | N/A | N/A | -50+450°c | TW-61130 |  |  | D1
8 | TE-61132 | TEMPERATURE ELEMENT | OIL FILTER (F-PK6101-1A/2A) OIL OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 3/4 | N/A | N/A | -50+450°c | TW-61132 |  |  | D1
9 | TE-61134 | TEMPERATURE ELEMENT | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 4/4 | N/A | N/A | -50+450°c | TW-61134 |  |  | D1
10 | TE-61137 | TEMPERATURE ELEMENT | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61137 |  |  | D1
11 | TE-61140 | TEMPERATURE ELEMENT | EVAPORATOR (E-6101) COLD HEXANE TUBE INLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 2/4 | N/A | N/A | -50+450°c | TW-61140 |  |  | D1
12 | TE-61141 | TEMPERATURE ELEMENT | OIL FILTER (F-PK6101-1B/2B) OIL OUTLET | N/A | NIS | ON THERMOWELL | N/A | N/A | RTD | 4/4 | N/A | N/A | -50+450°c | TW-61134 |  |  | D1
13 | TE-61142A | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1A MAIN MOTOR WINDING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 3/4 | N/A | ⁰C | 0~150 | MOTOR WINDING |  | NOTE 02 | D1
14 | TE-61142B | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1A MAIN MOTOR WINDING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 3/4 | N/A | ⁰C | 0~150 | MOTOR WINDING |  | NOTE 02 | D1
15 | TE-61142C | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1A MAIN MOTOR WINDING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 3/4 | N/A | ⁰C | 0~150 | MOTOR WINDING |  | NOTE 02 | D1
16 | TE-61143A | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1A MAIN MOTOR BEARING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 3/4 | N/A | ⁰C | 0~120 | MOTOR BEARING |  | NOTE 02 | D1
17 | TE-61143B | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1A MAIN MOTOR BEARING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 3/4 | N/A | ⁰C | 0~120 | MOTOR BEARING |  | NOTE 02 | D1
18 | TE-61143C | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1B MAIN MOTOR WINDING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 4/4 | N/A | ⁰C | 0~150 | MOTOR WINDING |  | NOTE 02 | D1
19 | TE-61144A | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1B MAIN MOTOR WINDING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 4/4 | N/A | ⁰C | 0~150 | MOTOR WINDING |  | NOTE 02 | D1
20 | TE-61144B | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1B MAIN MOTOR WINDING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 4/4 | N/A | ⁰C | 0~150 | MOTOR WINDING |  | NOTE 02 | D1
21 | TE-61145A | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1B MAIN MOTOR BEARING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 4/4 | N/A | ⁰C | 0~120 | MOTOR BEARING |  | NOTE 02 | D1
22 | TE-61145B | EMBEDED TEMPERATURE ELEMENT | C-PK6101-1B MAIN MOTOR BEARING EMBEDDED TEMPERATURE ELEMENT | AI | NIS | ON MOTOR | MCC | H | RTD | 4/4 | N/A | ⁰C | 0~120 | MOTOR BEARING |  | NOTE 02 | D1
F | TEMPERATURE TRANSMITTER
1 | TT-61122 | TEMPERATURE TRANSMITTER | ECONOMIZER (E-PK6101-3) PROPYLENE INLET TEMPERATURE CONTROL | AI | NIS | ON ELEMENT | 100UP-01 | H | 4-20 mA HART | 2/4 | N/A | ⁰C | -50~+50 | TE-61122 |  |  | D1
2 | TT-61125 | TEMPERATURE TRANSMITTER | EVAPORATOR (E-6101) COLD HEXANE TUBE OUTLET | AI | NIS | ON ELEMENT | 100UP-01 | H | 4-20 mA HART | 2/4 | N/A | ⁰C | -50~+50 | TE-61125 |  |  | D1
3 | TT-61130 | TEMPERATURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE OUTLET | AI | NIS | ON ELEMENT | 100UP-01 | H | 4-20 mA HART | 3/4 | N/A | ⁰C | 0~120 | TE-61130 |  |  | D1
4 | TT-61132 | TEMPERATURE TRANSMITTER | OIL FILTER (F-PK6101-1A/2A) OIL OUTLET | AI | NIS | ON ELEMENT | 100UP-01 | H | 4-20 mA HART | 3/4 | N/A | ⁰C | 0~120 | TE-61132 |  |  | D1
5 | TT-61134 | TEMPERATURE TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE OUTLET | AI | NIS | ON ELEMENT | 100UP-01 | H | 4-20 mA HART | 4/4 | N/A | ⁰C | 0~120 | TE-61134 |  |  | D1
6 | TT-61141 | TEMPERATURE TRANSMITTER | OIL FILTER (F-PK6101-1B/2B) OIL OUTLET | AI | NIS | ON ELEMENT | 100UP-01 | H | 4-20 mA HART | 4/4 | N/A | ⁰C | 0~120 | TE-61141 |  |  | D1
G | LEVEL GUAGE
1 | LG-61121 | LEVEL GAUGE (MAGNETIC) | LIQUID RECEIVER (D-PK6101-2) | N/A | NIS | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | MM | 0-1200 | D-PK6101-2 |  |  | D1
2 | LG-61122 | LEVEL GAUGE (MAGNETIC) | EVAPORATOR (E-6101) | N/A | NIS | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | MM | 0~2100 | E-6101 |  |  | D1
3 | LG-61126 | LEVEL GAUGE (MAGNETIC) | K.O DRUM (D-PK6101-3) | N/A | NIS | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | MM | 0~900 | D-PK6101-3 |  |  | D1
4 | LG-61128 | LEVEL GAUGE (MAGNETIC) | OIL SEPARATOR (D-PK6101-1A) | N/A | NIS | FIELD | N/A | N/A | N/A | 3/4 | PROPYLENE | MM | HOLD | D-PK6101-1A |  |  | D1
5 | LG-61130 | LEVEL GAUGE (MAGNETIC) | OIL SEPARATOR (D-PK6101-1B) | N/A | NIS | FIELD | N/A | N/A | N/A | 4/4 | PROPYLENE | MM | HOLD | D-PK6101-1B |  |  | D1
H | LEVEL TRANSMITTER
1 | LT-61120 | LEVEL TRANSMITTER (MAGNETIC) | LIQUID RECEIVER (D-PK6101-2) | AI | NIS | ON LG-61121 | 100UP-01 | H | 4-20 mA HART | 2/4 | N/A | MM | 0-100% | D-PK6101-2 |  |  | D1
2 | LT-61123 | LEVEL TRANSMITTER (MAGNETIC) | EVAPORATOR (E-6101) LEVEL MEASUREMENT & CONTROL | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | MM | 0-100% | E-6101 |  |  | D1
3 | LT-61125 | LEVEL TRANSMITTER (MAGNETIC) | K.O DRUM (D-PK6101-3) | AI | NIS | ON LG-61126 | 100UP-01 | H | 4-20 mA HART | 2/4 | N/A | MM | 0-100% | D-PK6101-3 |  |  | D1
4 | LT-61127 | LEVEL TRANSMITTER (MAGNETIC) | OIL SEPARATOR (D-PK6101-1A) | AI | NIS | ON LG-61127 | 100UP-01 | H | 4-20 mA HART | 3/4 | N/A | MM | HOLD | D-PK6101-1A |  |  | D1
5 | LT-61129 | LEVEL TRANSMITTER (MAGNETIC) | OIL SEPARATOR (D-PK6101-1B) | AI | NIS | ON LG-61130 | 100UP-01 | H | 4-20 mA HART | 4/4 | N/A | MM | HOLD | D-PK6101-1B |  |  | D1
I | VIBRATION TRANSMITTER
1 | VT-6120 | VIBRATION TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1A) VIBRATION | AI | NIS | COMPRESSOR | 100UP-01 | H | 4-20 mA | 3/4 | N/A | MM/S | 0-25,4 mm/s | C-PK6101-1A |  |  | D1
2 | VT-6121 | VIBRATION TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1B) VIBRATION | AI | NIS | COMPRESSOR | 100UP-01 | H | 4-20 mA | 4/4 | N/A | MM/S | 0-25,4 mm/s | C-PK6101-1B |  |  | D1
J | SLIDE VALVE INDICATOR
1 | ZI-61120 | SLIDE VALVE POSITION INDICATOR | SCREW COMPRESSOR (C-PK6101-1A) CAPACITY CONTROL SLIDE VALVE | N/A | NIS | ON ELEMENT | N/A | N/A | N/A | 3/4 | N/A | N/A | 0-100% | ZT-61120 |  |  | D1
2 | ZI-61121 | SLIDE VALVE POSITION INDICATOR | SCREW COMPRESSOR (C-PK6101-1B) CAPACITY CONTROL SLIDE VALVE | N/A | NIS | ON ELEMENT | N/A | N/A | N/A | 3/4 | N/A | N/A | 0-100% | ZT-61121 |  |  | D1
K | SLIDE VALVE TRANSMITTER
1 | ZT-61120 | SLIDE VALVE POSITION TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1A) CAPACITY CONTROL SLIDE VALVE | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA | 3/4 | N/A | N/A | 0-100% | CAPACITY CONTROL SLIDE VALVE |  |  | D1
2 | ZT-61121 | SLIDE VALVE POSITION TRANSMITTER | SCREW COMPRESSOR (C-PK6101-1B) CAPACITY CONTROL SLIDE VALVE | AI | NIS | FIELD | 100UP-01 | H | 4-20 mA | 3/4 | N/A | N/A | 0-100% | CAPACITY CONTROL SLIDE VALVE |  |  | D1
L | LIMIT SWITCHES
1 | XZSL-61124 | VALVE LIMIT SWITCH | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61124 |  |  | D1
2 | XZSH-61124 | VALVE LIMIT SWITCH | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61124 |  |  | D1
3 | TS-61133A | TEMPERATURE SWITCH | OIL HEATER (E-PK6101-4A) OVER-TEMPERATURE CUT-OUT SWITCH | DI | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | N/A | ⁰C | 100°c | ON OIL HEATER |  |  | D1
4 | TS-61133B | TEMPERATURE SWITCH | OIL HEATER (E-PK6101-4A) OVER-TEMPERATURE SWITCH | DI | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | N/A | ⁰C | 80°c | ON OIL HEATER |  |  | D1
5 | TS-61133C | TEMPERATURE SWITCH | OIL HEATER (E-PK6101-4A) THERMOSTATIC SWITCH | DI | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | N/A | ⁰C | 45°c | ON OIL HEATER |  |  | D1
6 | XZSL-61134 | VALVE LIMIT SWITCH | EVAPORATOR (E-6101) PROPYLENE SHELL INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61121 |  |  | D1
7 | XZSH-61134 | VALVE LIMIT SWITCH | EVAPORATOR (E-6101) PROPYLENE SHELL INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61121 |  |  | D1
8 | XZSL-61135 | VALVE LIMIT SWITCH | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61120 |  |  | D1
9 | XZSH-61135 | VALVE LIMIT SWITCH | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61120 |  |  | D1
10 | XZSL-61136 | VALVE LIMIT SWITCH | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61136 |  |  | D1
11 | XZSH-61136 | VALVE LIMIT SWITCH | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE INLET | DI | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | N/A | N/A | N/A | XV-61136 |  |  | D1
12 | TS-61136A | TEMPERATURE SWITCH | OIL HEATER (E-PK6101-4A) OVER-TEMPERATURE CUT-OUT SWITCH | DI | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | N/A | ⁰C | 100°c | ON OIL HEATER |  |  | D1
13 | TS-61136B | TEMPERATURE SWITCH | OIL HEATER (E-PK6101-4A) OVER-TEMPERATURE SWITCH | DI | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | N/A | ⁰C | 80°c | ON OIL HEATER |  |  | D1
14 | TS-61136C | TEMPERATURE SWITCH | OIL HEATER (E-PK6101-4A) THERMOSTATIC SWITCH | DI | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | N/A | ⁰C | 45°c | ON OIL HEATER |  |  | D1
M | VALVE BODY
1 | XV-61121 | VALVE BODY & ACTUATOR | EVAPORATOR (E-6101) PROPYLENE SHELL INLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 6"-PR-61130-1DL4-M |  |  | D0
2 | XV-61124 | VALVE BODY & ACTUATOR | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE INLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 6"-PR-61128-1DL4-M |  |  | D0
3 | XV-61135 | VALVE BODY & ACTUATOR | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE INLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 3"-PR-61126-1DL4-M |  |  | D0
4 | XV-61136 | VALVE BODY & ACTUATOR | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE INLET | N/A | N/A | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | N/A | N/A | 6"-PR-61127-1DL4-M |  |  | D0
N | SOLENOID VALVE
1 | SOV-61120A | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1A) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | OIL | N/A | N/A | OIL LOAD RETURN TUBE |  |  | D1
2 | SOV-61120B | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1A) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | OIL | N/A | N/A | OIL UNLOAD SUPPLY TUBE |  |  | D1
3 | SOV-61120C | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1A) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | OIL | N/A | N/A | OIL LOAD SUPPLY TUBE |  |  | D1
4 | SOV-61120D | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1A) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | OIL | N/A | N/A | OIL UNLOAD RETURN TUBE |  |  | D1
5 | SOV-61121A | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1B) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | OIL | N/A | N/A | OIL LOAD RETURN TUBE |  |  | D1
6 | SOV-61121B | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1B) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | OIL | N/A | N/A | OIL UNLOAD SUPPLY TUBE |  |  | D1
7 | SOV-61121C | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1B) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | OIL | N/A | N/A | OIL LOAD SUPPLY TUBE |  |  | D1
8 | SOV-61121D | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1B) CAPACITY CONTROL SLIDE VALVE | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | OIL | N/A | N/A | OIL UNLOAD RETURN TUBE |  |  | D1
9 | SOV-61122 | SOLENOID VALVE | K.O DRUM (D-PK6101-3) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 2/4 | OIL | N/A | N/A | K.O. DRUM OIL DRAIN LINE |  |  | D1
10 | SOV-61123 | SOLENOID VALVE | OIL SEPARATOR (D-PK6101-1A) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 2/4 | OIL | N/A | N/A | CONDENSER LINE |  |  | D1
11 | XSOV-61124 | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1B) PROPYLENE INLET | DO | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | INSTRUMENT AIR | N/A | N/A | XV-61124 |  |  | D1
12 | SOV-61125 | SOLENOID VALVE | OIL SEPARATOR (D-PK6101-1A) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | OIL | N/A | N/A | OIL SEPARATOR OUTLET TUBE |  |  | D1
13 | SOV-61126 | SOLENOID VALVE | OIL SEPARATOR (D-PK6101-1A) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | OIL | N/A | N/A | OIL SEPARATOR OUTLET TUBE |  |  | D1
14 | SOV-61127 | SOLENOID VALVE | OIL SEPARATOR (D-PK6101-1B) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | OIL | N/A | N/A | OIL SEPARATOR OUTLET TUBE |  |  | D1
15 | SOV-61128 | SOLENOID VALVE | OIL SEPARATOR (D-PK6101-1B) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | OIL | N/A | N/A | OIL SEPARATOR OUTLET TUBE |  |  | D1
16 | SOV-61129 | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1A) OIL INLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 2/4 | OIL | N/A | N/A | COMPRESSOR B INLET OIL LINE |  |  | D1
17 | SOV-61130 | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1B) OIL INLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 2/4 | OIL | N/A | N/A | COMPRESSOR A INLET OIL LINE |  |  | D1
18 | SOV-61131 | SOLENOID VALVE | OIL COOLER (E-PK6101-1A) JACKET WATER OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 3/4 | JACKET WATER | N/A | N/A | 3"-JWR-61121-4CC2-. |  |  | D1
19 | SOV-61132 | SOLENOID VALVE | OIL COOLER (E-PK6101-1B) JACKET WATER OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 4/4 | JACKET WATER | N/A | N/A | 3"-JWR-61122-4CC2-. |  |  | D1
20 | SOV-61133 | SOLENOID VALVE | EVAPORATOR (E-6101) OIL OUTLET | DO | NIS | FIELD | 100UP-01 | H | 24 VDC | 2/4 | OIL | N/A | N/A | EVAPORATOR OIL DRAIN LINE |  |  | D1
21 | XSOV-61134 | SOLENOID VALVE | EVAPORATOR (E-6101) PROPYLENE SHELL INLET | DO | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | INSTRUMENT AIR | N/A | N/A | XV-61121 |  |  | D1
22 | XSOV-61135 | SOLENOID VALVE | ECONOMIZER (E-PK6101-3) PROPYLENE TUBE INLET | DO | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | INSTRUMENT AIR | N/A | N/A | XV-61120 |  |  | D1
23 | XSOV-61136 | SOLENOID VALVE | SCREW COMPRESSOR (C-PK6101-1A) PROPYLENE INLET | DO | NIS | ON VALVE | 100UP-01 | H | 24 VDC | 2/4 | INSTRUMENT AIR | N/A | N/A | XV-61136 |  |  | D1
O | CONTROL VALVES (Others)
1 | TV-61122 | CONTROL VALVE | ECONOMIZER (E-PK6101-3) PROPYLENE INLET TEMPERATURE MEASUREMENT & CONTROL | AO | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | N/A | 0~100% | 3"-PR-61126-1DL4-M |  |  | D1
2 | LV-61123 | CONTROL VALVE | EVAPORATOR (E-6101) LEVEL MEASUREMENT & CONTROL | AO | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | N/A | 0~100% | 6"-PR-61130-1DL4-M |  |  | D1
3 | PV-61126 | CONTROL VALVE | K.O DRUM (D-PK6101-3) PROPYLENE OUTLET PRESSURE MEASUREMENT & CONTROL | AO | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 2/4 | PROPYLENE | N/A | 0~100% | 12"-PR-61136-1DL4-M |  |  | D1
4 | TCV-61131 | TEMPERATURE REGULATOR | OIL COOLER (E-PK6101-1A) OIL SHELL OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 3/4 | OIL | ⁰C | 50°c | 3"-OIL-61122-1DL4-E |  |  | D1
5 | PV-61135 | CONTROL VALVE | OIL SEPARATOR (D-PK6101-1A) PROPYLENE OUTLET PRESSURE MEASUREMENT & CONTROL | AO | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 3/4 | PROPYLENE | N/A | 0~100% | 6"-PR-61138-1DL4-P |  |  | D1
6 | TCV-61135 | TEMPERATURE REGULATOR | OIL COOLER (E-PK6101-1A) OIL SHELL OUTLET | N/A | N/A | FIELD | N/A | N/A | N/A | 4/4 | OIL | ⁰C | 50°c | 3"-OIL-61132-1DL4-E |  |  | D1
7 | PV-61150 | CONTROL VALVE | OIL SEPARATOR (D-PK6101-1B) PROPYLENE OUTLET PRESSURE MEASUREMENT & CONTROL | AO | NIS | FIELD | 100UP-01 | H | 4-20 mA HART | 4/4 | PROPYLENE | N/A | 0~100% | 6"-PR-61138-1DL4-P |  |  | D1
8 | II-61101 | MAIN MOTOR CURRENT | MAIN MOTOR COMPRESSOR (C-PK6101-1A) | AI | NIS | ON MOTOR | 100UP-01 | H | 4-20 mA HART | 3/4 | CURRENT | AMP | 0-200Amp | MAIN MOTOR |  |  | D1
9 | II-61102 | MAIN MOTOR CURRENT | MAIN MOTOR COMPRESSOR (C-PK6101-1B) | AI | NIS | ON MOTOR | 100UP-01 | H | 4-20 mA HART | 4/4 | CURRENT | AMP | 0-200Amp | MAIN MOTOR |  |  | D1
P | RELIEF VALVES | [15 empty] | D0
1 | PSV-61120 | PRESSURE SAFETY VALVE | LIQUID RECEIVER (D-PK6101-2) | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 4"-PR-61124-1DL4-N |  |  | D0
2 | PSV-61121 | PRESSURE SAFETY VALVE | ECONOMIZER (E-PK6101-3) PROPYLENE OUTLET | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 4"-PR-61129-1DL4-N |  |  | D0
3 | PSV-61122 | PRESSURE SAFETY VALVE | ECONOMIZER (E-PK6101-3) | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 6"-PR-61131-1DL4-N |  |  | D0
4 | PSV-61123 | PRESSURE SAFETY VALVE | EVAPORATOR (E-6101) PROPYLENE OUTLET | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 4"-PR-61137-1DL4-N |  |  | D0
5 | PSV-61124 | PRESSURE SAFETY VALVE | K.O DRUM (D-PK6101-3) PROPYLENE OUTLET | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 2"-PR-61139-1DL4-N |  |  | D0
6 | PSV-61125 | PRESSURE SAFETY VALVE | OIL SEPARATOR (D-PK6101-1A) | N/A |  | FIELD | N/A | N/A | N/A | 3/4 | PROPYLENE | BARG | 23 | 6"-PR-61143-1DL4-N |  |  | D0
7 | PRV-61126 | PRESSURE RELIEF VALVE | OIL PUMP (P-PK6101-1A) DISCHARGE | N/A |  | ON PUMP | N/A | N/A | N/A | 3/4 | OIL | BARG | 2.5 | P-PK6101-2A | N/A | Integrated in Oil Gear Pump | D0
8 | PRV-61127 | PRESSURE RELIEF VALVE | OIL PUMP (P-PK6101-2A) DISCHARGE | N/A |  | ON PUMP | N/A | N/A | N/A | 3/4 | OIL | BARG | 2.5 | P-PK6101-2A | N/A | Integrated in Oil Gear Pump | D0
9 | PSV-61128 | PRESSURE SAFETY VALVE | OIL SEPARATOR (D-PK6101-1B) | N/A |  | FIELD | N/A | N/A | N/A | 4/4 | PROPYLENE | BARG | 23 | 6"-PR-61145-1DL4-N |  |  | D0
10 | PRV-61129 | PRESSURE RELIEF VALVE | OIL PUMP (P-PK6101-1B) DISCHARGE | N/A |  | ON PUMP | N/A | N/A | N/A | 4/4 | OIL | BARG | 2.5 | P-PK6101-2B | N/A | Integrated in Oil Gear Pump | D0
11 | PRV-61130 | PRESSURE RELIEF VALVE | OIL PUMP (P-PK6101-2B) DISCHARGE | N/A |  | ON PUMP | N/A | N/A | N/A | 4/4 | OIL | BARG | 2.5 | P-PK6101-2B | N/A | Integrated in Oil Gear Pump | D0
12 | PSV-61131 | PRESSURE SAFETY VALVE | LIQUID RECEIVER (D-PK6101-2) | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 4"-PR-61147-1DL4-N |  |  | D0
13 | PSV-61132 | PRESSURE SAFETY VALVE | EVAPORATOR (E-6101) PROPYLENE OUTLET | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 4"-PR-61148-1DL4-N |  |  | D0
14 | PSV-61133 | PRESSURE SAFETY VALVE | K.O DRUM (D-PK6101-3) PROPYLENE OUTLET | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 2"-PR-61149-1DL4-N |  |  | D0
15 | PSV-61134 | PRESSURE SAFETY VALVE | CONDENSER (E-PK6101-2) JACKET WATER RETURN TUBE OUTLET | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | JACKET WATER | BARG | 10 | 12"-JWR-61120-4CC2-N |  |  | D0
16 | PSV-61135 | PRESSURE SAFETY VALVE | ECONOMIZER (E-PK6101-3) | N/A |  | FIELD | N/A | N/A | N/A | 2/4 | PROPYLENE | BARG | 23 | 6"-PR-61151-1DL4-N |  |  | D1
Note 01: Manufacturer & Model will be filled by approved and supplied equipment in final revision of instrument index list.
Note 02: Main motor winding temperature elements are located on the main motor terminal box and are required to be wired directly to MCC for proper protection. Customer to confirm if no transmitter is required due to distance from MCC to package.
POI: IFA
Rev.: D1