| Comment sheet based on agreement with client |  |  |  |
| --- | --- | --- | --- |
| NO. | PURCHASER’S COMMENTS | VENDOR’S REPLY | Conclusion |
|  | Please confirm that compressor will be design based on API 610 5th editon with deviation which has been sent during bid stage |  |  |
|  | Please clarify the standard of test and ITP for motors. Generally standard of test for motors as per project requirement is IEC. Please see attachment#1 for ITP based on comment of client. Also please delete items which cannot be done by vendor. |  |  |
|  | Two electric oil pumps (one in operation and other as standby) shall be considered. |  |  |
|  | In case of not following project PMS inside package, then vendor shall issue its own PMS inside package |  |  |
|  | Revised offer based on agreement of TCL shall be received from MYCOM. Also, in case of discrepancy between revised offer and TCL, all items in TCL are in priority. |  |  |
|  | Revised PFD and P&ID shall be sent by vendor (by pass line and accessories shall be shown). |  |  |
|  | Compressor model shall be clarified by vendor. |  |  |
|  | PFD with all data especially utility shall be revised based on comment in TCL. |  |  |
|  | VI range for compressor shall be specified by vendor. |  |  |
|  | Vendor shall send procedure for changeover of compressors during normal operation. |  |  |
|  | Latest TCL shall be replied by MYCOM. |  |  |
|  | Preliminary GA DWG including location of equipment, dimension and weight shall be specified. |  |  |
|  | Material selection diagram shall be sent by vendor. |  |  |
|  | ESD and F&G Diagrams for Package and relation with other Section shall be sent by vendor. |  |  |
|  | Revised offer and data sheet of each equipment shall be sent by vendor. |  |  |
|  | Project symbol and legend configuration 1 shall be followed by vendor. |  |  |
|  | Filter and dryer for makeup of refrigerant shall be shown in P&ID. |  |  |
|  | Hot redundancy shall be considered for both compressors. |  |  |