| Comment sheet based on agreement with client |  |  |  |
| --- | --- | --- | --- |
| NO. | PURCHASER’S COMMENTS | VENDOR’S REPLY | Conclusion |
|  | Please confirm that compressor will be design based on API 619 5th editon with deviation which has been sent during bid stage | Compressor will be as per API 619 as per provided deviations |  |
|  | Please clarify the standard of test and ITP for motors. Generally standard of test for motors as per project requirement is IEC. Please see attachment#1 for ITP based on comment of client. Also please delete items which cannot be done by vendor. | Test reports will be provided and it will be as per IEC standard. Reference ITP has been provided during clarification stage. For Compressor unit MYCOM provided ITP will be followed, for local portion ITP discussed in Bid stage will be followed by vendor .It can be agreed in Pre inspection Meeting. |  |
|  | Two electric oil pumps (one in operation and other as standby) shall be considered. | Noted Confirmed |  |
|  | In case of not following project PMS inside package, then vendor shall issue its own PMS inside package | Noted |  |
|  | Revised offer based on agreement of TCL shall be received from MYCOM. Also, in case of discrepancy between revised offer and TCL, all items in TCL are in priority. | Engineering documents will be issued during detail design based on agreements made in Technical clarification as the highest priority. |  |
|  | Revised PFD and P&ID shall be sent by vendor (by pass line and accessories shall be shown). | Engineering documents will be issued during detail design based on agreements made in Technical clarification as the highest priority. |  |
|  | Compressor model shall be clarified by vendor. | 320L Model is the selected Model. Project is fully custom designed as per project need. |  |
|  | PFD with all data especially utility shall be revised based on comment in TCL. | Engineering documents will be issued during detail design based on agreements made in Technical clarification as the highest priority. |  |
|  | VI range for compressor shall be specified by vendor. | Compressor capacity is from 30%-100% using capacity controller and for 0-30% Hot gas by pass line has been considered. VI range to be provided in detail engineering |  |
|  | Vendor shall send procedure for changeover of compressors during normal operation. | It will be provided during Engineering Phase |  |
|  | Latest TCL shall be replied by MYCOM. | Noted. You may find attached our reply. |  |
|  | Preliminary GA DWG including location of equipment, dimension and weight shall be specified. | It will be provided during detail engineering, reference GA has been provided. |  |
|  | Material selection diagram shall be sent by vendor. | Materials has been specified in TCL and offer, Respective equipment datasheet will be provided during engineering stage |  |
|  | ESD and F&G Diagrams for Package and relation with other Section shall be sent by vendor. | These will be discussed during detail design in will be provided in PID |  |
|  | Revised offer and data sheet of each equipment shall be sent by vendor. | We will follow agreed TCL as the highest priority |  |
|  | Project symbol and legend configuration 1 shall be followed by vendor. | Noted for local parts, for compressor units as far as possible |  |
|  | Filter and dryer for makeup of refrigerant shall be shown in P&ID. | During detail design |  |
|  | Hot redundancy shall be considered for both compressors. | Noted. |  |