## Attachment 7- Close out Report
Company: EIED
Consultant: Arya Imen Tadbir
Recommendations / H.S.E Reply | References | Responsibility | Diciplines | [6 empty] | Item (Open/Close) | Deadlines | Signature
|  |  | Process | Instrument | Piping | Machinery | Mechanic | General Engineering | HSE
Check for considering pressure differential gauge for C-6101A, and C-6101B suction strainers. | REF#01 | H.S.E. | Pressure differential gauge is not required due to below provisions: 1. The system is a closed loop with propylene refrigerant that is is normally a solvent. 2. There is a pressure transmitter that detects low and low-low pressure 3. With low suction pressure, discharge pressure drops as the compressors cannot maintain it. 4. Chiller outlet temperature will increase, causing an alarm and trip.
Consider emergency depressurizing system with ESD system (I.e. blow down valve) for the refrigeration system. Check study/ for considering a shut down with depressurizing, and a shut down without depressurizing. | REF#02 | H.S.E./EIED | As per API-521, section 4.6.4, emergency depressuring is required for large process equipment operating at a gauge pressure of 1700 kPa (~250 psi) or higher. For this package, equalize pressure after compressor shutdown is about 1140 kPag which is less than the required pressure in API-521. So emergency depressuring is not applicable for this package.
Consider Thermal Relief Valve (TRV) for cooling water line of E-6104. Or, remove isolating block valves on cooling water lines of E-6104 (due to presence of PSV-61101-R in PID-611B). | REF#03 | H.S.E. | Isolating block valve on cooling water line will be removed.
Consider independent pressure transmitters with low low alarm with ESD system for suction C-6101A, and C-6101B. Or, perform SIL study for the refrigeration package. | REF#04 | H.S.E. | There is no need to have a transmitter as the recycle valve is used only during start up and very low flow. Also, contractual minimum flow (10% capacity) does not require this recycle valve to operate. Although it is not necessary, but Pressure Transmitter for suction of C-6101A, and C-6101B of will be supplied with SIL2 certificate. | There is no need to have a transmitter as the recycle valve is used only during start up and very low flow. Also, contractual minimum flow (10% capacity) does not require this recycle valve to operate. Although it is not necessary, but Pressure Transmitter for suction of C-6101A, and C-6101B of will be supplied with SIL2 certificate.
Consider temperature and pressure gauges for (as a minimum), transmitters which initiate compressors shut down (including compressor suction and discharge pressure, and oil separator temperature). | REF#05 | H.S.E. |  | It is not needed as there is an indicator on all transmitters and in case of failure of one transmitter, there are other safeguards. Although this recommendation is only a preference and there is no consequences, anyhow for client satisfaction, PG on suction pressure and discharge pressure and TG on oil separator will be added.
Consider Thermal Relief Valve (TRV) for cooling water line of E-6102. Or, remove isolating block valves on cooling water lines of E-6102 (due to presence of PSV-61101-R in PID-611B). | REF#06 | H.S.E. | Isolating block valve on cooling water line will be removed.
Consider temperature and pressure gauges for (as a minimum), transmitters which initiate compressors shut down (including lube oil temperature downstream of the oil filter, lube oil pressure). | REF#07 | H.S.E. |  | It is not needed as there is an indicator on all transmitters and in case of failure of one transmitter, there are other safeguards. Although this recommendation is only a preference and there is no consequences, anyhow for client satisfaction, PG on oil supply and and TG on downstream of filter will be added.