## AllPages
CLIENT DOC.: VD-GPIC-MA-3029-3029-0045
I/O LIST: PLC, ESD & VMS | [8 empty] | ULTIM DOC.: ULT003-30070
CLIENT: | [8 empty] | DELTA
P.O. No.: | [8 empty] | GPIC DD MA REQ 000 3029
PROJECT: | [8 empty] | -----
SERVICE: | [8 empty] | PROPYLENE REFRIGERATION UNIT
UNIT: | [8 empty] | PK-6101
REV | DATE |  |  | PREPARED BY |  | CHECKED BY |  |  | DESCRIPTION
0 | 27/06/2025 |  |  | FAD |  | IMA |  |  | FOR APPROVAL
1 | 24/10/2025 |  |  | FAD |  | IMA |  |  | FOR APPROVAL
2 | 28/12/2025 |  |  | FAD |  | IMA |  |  | FOR APPROVAL
3 | 14/02/2026 |  |  | FAD |  | IMA |  |  | FOR APPROVAL
ULT003 - PLC I/O LIST COUNT IS PER UNIT
|  | AI : Analog Input AO : Analog Input H : Hardwire S : Serial DI: Digital Input DO: Digital Output DCS : Data Control Center MCC : Motor Control Center UCP-6101 : Unit Control Panel LCP : Local Control Station PLC : Programmable Logic Controller PW400 : POWER SUPPLY 400 W This IO List is a document containing list of instrumentation which serve as input or output of control system. | [5 empty] | AIR: Analog Input Redundancy AOR: Analog Output Redundancy DIR: Digital Input Redundancy DOR: Digital Output Redundancy NO: Normally Open NC: Normally Close NDE: Normally De- Energize NE: Normally Energize
STATES
TAG |  | SERVICE | PID DWG No. |  | TYPE | FROM | TO | DESCRIPTION |  | Engineering units | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL | CONTACT TYPE | POWER SUPPLY | TYPE | SERIAL | IS/NIS | RACK | SLOT | CHANNEL | STATES'0' | STATES'1'
Card Type: Digital IN/ 16
TAG |  | SERVICE | PID DWG No. |  |  |  |  | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
XA- 61199 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | UPS AC SUPPLY 1 SURGE PROTECTION OK |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 0 | OFF | ON
XA- 61198 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | UPS AC SUPPLY 2 SURGE PROTECTION OK |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 1 | OFF | ON
XA- 61190 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | LOGIC POWER SUPPLY # 1 OK |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 2 | OFF | ON
XA- 61191 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | LOGIC POWER SUPPLY # 2 OK |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 3 | OFF | ON
XA- 61192 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | I/O POWER SUPPLY # 1 OK |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 4 | OFF | ON
XA- 61193 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | I/O POWER SUPPLY # 2 OK |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 5 | OFF | ON
HS-61161 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | PLC | ESD |  |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 6
[8 empty] | SPARE | [11 empty] | 2 | 2 | 7
HS-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | EMERGENCY STOP PB. |  |  | COMP A SKID | LCP-6101A | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 2 | 8 | OFF | ON
HST-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | COMPRESSOR -A- LOCAL START PB |  |  | COMP A SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 2 | 9 | OFF | ON
HSP-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | COMPRESSOR -A- LOCAL STOP PB |  |  | COMP A SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 2 | 10 | OFF | ON
[8 empty] | SPARE | [11 empty] | 2 | 2 | 11
HST-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101B | UCP-6101 | COMPRESSOR -B- LOCAL START PB |  |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 2 | 12 | OFF | ON
HSP-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101B | UCP-6101 | COMPRESSOR -B- LOCAL STOP PB |  |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 2 | 13 | OFF | ON
ESD-61010 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | ESD | PLC | ESD |  |  | ESD | UCP-6101 | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 2 | 14 | OFF | ON
[8 empty] | SPARE | [11 empty] | 2 | 2 | 15
Card Type: Digital IN/ 16
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
HSLR-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | COMPRESSOR -A- LOCAL -REMOTE SELECTOR |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 3 | 0 | OFF | ON
HSLR-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101B | UCP-6101 | COMPRESSOR -B- LOCAL -REMOTE SELECTOR |  |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 3 | 1 | OFF | ON
HS-C6101AL |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | LAMP TEST ON LCPA |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 3 | 2 | OFF | ON
HS-C6101BL |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101B | UCP-6101 | LAMP TEST ON LCPB |  |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 3 | 3 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 4
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 5
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 6
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 7
ZSH-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | FIELD | UCP-6101 | COMPRESSOR -A- SLIDE VALVE 100% |  |  | COMP -A- SKID | JB-UIA-61111 | DI | 24VDC | NO | PW400 | H |  | IS | 2 | 3 | 8 | OFF | ON
ZSL-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | FIELD | UCP-6101 | COMPRESSOR -A- SLIDE VALVE 0% |  |  | COMP -A- SKID | JB-UIA-61111 | DI | 24VDC | NO | PW400 | H |  | IS | 2 | 3 | 9 | OFF | ON
ZSH-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | FIELD | UCP-6101 | COMPRESSOR -B- SLIDE VALVE 100% |  |  | COMP -B- SKID | JB-UIA-61121 | DI | 24VDC | NO | PW400 | H |  | IS | 2 | 3 | 10 | OFF | ON
ZSL-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | FIELD | UCP-6101 | COMPRESSOR -B- SLIDE VALVE 0% |  |  | COMP -B- SKID | JB-UIA-61121 | DI | 24VDC | NO | PW400 | H |  | IS | 2 | 3 | 11 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 12
YSLH-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | COMPRESSOR -B- RUNNING |  |  | MCC | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 3 | 13 | OFF | ON
YSLF-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | COMPRESSOR -B- FAULT |  |  | MCC | UCP-6101 | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 3 | 14 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 15
Card Type: Digital IN/ 16
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
YSLH-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | COMPRESSOR -A- RUNNING |  |  | MCC | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 4 | 0 | OFF | ON
YSLF-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | COMPRESSOR -A- FAULT |  |  | MCC | UCP-6101 | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 1 | OFF | ON
YSLH-EH6101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | OIL HEATER RUNNING |  |  | MCC | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 4 | 2 | OFF | ON
YSLF-EH6101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6102 | OIL HEATER - FAULT |  |  | MCC | UCP-6101 | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 3 | OFF | ON
YSLH-P6111A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | PUMP A RUNNING |  |  | MCC | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 4 | 4 | OFF | ON
YSLF-P6111A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | PUMP A - FAULT |  |  | MCC | UCP-6101 | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 5 | OFF | ON
YSLH-P6111B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | PUMP B RUNNING |  |  | MCC | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 4 | 6 | OFF | ON
YSLF-P6111B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | MCC | UCP-6101 | PUMP B - FAULT |  |  | MCC | UCP-6101 | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 7 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 | H |  | NIS | 2 | 4 | 8
[8 empty] | SPARE |  |  |  |  | DI | 24VDC | - | PW400 |  |  |  | 2 | 4 | 9
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 4 | 10
HS-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101B | UCP-6101 | EMERGENCY STOP PB. |  |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 11 | OFF | ON
YLH-P6111A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101A | PUMP A RUNNING |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 4 | 12 | OFF | ON
YL-P6111A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101A | PUMP A - FAULT |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 13 | OFF | ON
YLH-P6111B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101A | PUMP B RUNNING |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 4 | 14 | OFF | ON
YL-P6111B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101A | PUMP B - FAULT |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NC | PW400 | H |  | NIS | 2 | 4 | 15 | OFF | ON
Card Type: Digital IN/ 16
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
HS-P6111A/B-A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | LEAD/LAG - PUMP A - SELECTOR |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 0 | OFF | ON
HS-P6111A/B-B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | LEAD/LAG - PUMP B - SELECTOR |  |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 1 | OFF | ON
HSLR-P6111A-1 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | HOA-HAND - PUMP A |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 2 | OFF | ON
HSLR-P6111A-2 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6102 | HOA-OFF - PUMP A |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 3 | OFF | ON
HSLR-P6111A-3 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | HOA-AUTO - PUMP A |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 4 | OFF | ON
HST-P6111A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | PUMP A LOCAL START PB |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 5 | OFF | ON
HSP-P6111A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | PUMP A LOCAL STOP PB |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 6 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DI | 24VDC | - | PW400 |  |  |  | 2 | 5 | 7
HSLR-P6111B-1 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | HOA-HAND - PUMP B |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 8 | OFF | ON
HSLR-P6111B-2 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6102 | HOA-OFF - PUMP B |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 9 | OFF | ON
HSLR-P6111B-3 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | HOA-AUTO - PUMP B |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 10 | OFF | ON
HST-P6111B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | PUMP B LOCAL START PB |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 11 | OFF | ON
HSP-P6111B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | LCP-6101A | UCP-6101 | PUMP B LOCAL STOP PB |  |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 12 | OFF | ON
TS-6101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | DCS | UCP-6101 | TIME SYNCHRONIZATION |  |  | DCS | UCP-6101 | DI | 24VDC | NO | PW400 | H |  | NIS | 2 | 5 | 13
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 5 | 14
[8 empty] | SPARE |  |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 5 | 15
ULT003 - PLC I/O LIST COUNT IS PER UNIT
|  | AI : Analog Input AO : Analog Input H : Hardwire S : Serial DI: Digital Input DO: Digital Output DCS : Data Control Center MCC : Motor Control Center UCP-6101 : Unit Control Panel LCP : Local Control Station PLC : Programmable Logic Controller PW400 : POWER SUPPLY 400 W This IO List is a document containing list of instrumentation which serve as input or output of control system. | [5 empty] | AIR: Analog Input Redundancy AOR: Analog Output Redundancy DIR: Digital Input Redundancy DOR: Digital Output Redundancy NO: Normally Open NC: Normally Close NDE: Normally De- Energize NE: Normally Energize
STATES
TAG |  | SERVICE | PID DWG No. |  | TYPE | FROM | TO | DESCRIPTION |  | Engineering units | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL | RELAY OUTPUT | POWER SUPPLY | TYPE | SERIAL | IS/NIS | RACK | SLOT | CHANNEL | STATES'0' | STATES'1'
Card Type: Digital OUT/ 16
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
YLH-6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101A | COMPRESSOR -A- RUNNING |  |  | COMP SKID | LCP-6101A | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 0 | OFF | ON
YL-6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101A | COMPRESSOR -A- AVAILABLE/FAULT |  |  | COMP SKID | LCP-6101A | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 1 | OFF | ON
YLH-6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101B | COMPRESSOR -B- RUNNING |  |  | COMP SKID | LCP-6101A | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 2 | OFF | ON
YL-6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | LCP-6101B | COMPRESSOR -B- AVAILABLE/FAULT |  |  | COMP SKID | LCP-6101A | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 3 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 4
XA- 61195 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | UCP-6101 | ENCLOSURE FANS ON/OFF - 1 |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 6 | 5 | OFF | ON
HSL-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | COMPA. START COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 6
HSH-C6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | COMPA. STOP COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 7
HSL-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | COMPB. START COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 8
HSH-C6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | COMPB. STOP COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 9
HSL-P6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | PUMP.A. START COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 10
HSH-P6101A |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | PUMP.A. STOP COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 11
HSL-P6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | PUMP.B START COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 12
HSH-P6101B |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | PUMP.B. STOP COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 13
HSL-EH6101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | ELEC.HEATER. START COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 14
HSH-EH6101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | MCC | ELEC.HEATER. STOP COMMAND TO MCC |  |  | MCC | UCP-6101 | DO | 24VDC | NDE | PW400 | H |  | NIS | 2 | 6 | 15
Card Type: Digital OUT/ 16
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
XY-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | FIELD | COMPRESSOR -A- SLIDE VALVE UNLOAD SOV |  |  | COMP SKID | JB-UEV-612 | DO | 24VDC | NE | PW400 | H |  | NIS | 2 | 7 | 0 | OFF | ON
XY-61112 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | FIELD | COMPRESSOR -A- SLIDE VALVE LOAD SOV |  |  | COMP SKID | JB-UEV-612 | DO | 24VDC | NE | PW400 | H |  | NIS | 2 | 7 | 1 | OFF | ON
XY-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | FIELD | COMPRESSOR -B- SLIDE VALVE UNLOAD SOV |  |  | COMP SKID | JB-UEV-622 | DO | 24VDC | NE | PW400 | H |  | NIS | 2 | 7 | 2 | OFF | ON
XY-61122 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | FIELD | COMPRESSOR -B- SLIDE VALVE LOAD SOV |  |  | COMP SKID | JB-UEV-622 | DO | 24VDC | NE | PW400 | H |  | NIS | 2 | 7 | 3 | OFF | ON
XY-61151 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | FIELD | OIL RECOVERY VALVE SOV - COMPRESSOR DISCHARGE |  |  | VESSELS SKID | JB-UEV-652 | DO | 24VDC | NE | PW400 | H |  | NIS | 2 | 7 | 0 | OFF | ON
XY-61152 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | FIELD | OIL RECOVERY VALVE SOV - CHILLER RECOVERY |  |  | VESSELS SKID | JB-UEV-652 | DO | 24VDC | NE | PW400 | H |  | NIS | 2 | 7 | 1 | OFF | ON
[8 empty] | SPARE |  |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 2
[8 empty] | SPARE |  |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 3
[8 empty] | SPARE |  |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 4
[8 empty] | SPARE |  |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 5
XA-61101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | DCS | COMPRESSOR -A- ALRM COMPRESSOR |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | NDE | PW400 | H | S | NIS | 2 | 7 | 6 | OFF | ON
XA-61102 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | DCS | COMMON -A- TRIP COMPRESSOR |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | NDE | PW400 | H | S | NIS | 2 | 7 | 7 | OFF | ON
XA-61103 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | DCS | COMPRESSOR -B- TRIP COMPRESSOR |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 8 | OFF | ON
XA-61104 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | DCS | COMMON -B- ALRM COMPRESSOR |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 9 | OFF | ON
UA-61199 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | DCS | INTERLOCK ACTIVATED FOR COMP. B |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 10 | OFF-PULSE | ON-PULSE
UA-61114 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | BOOL | UCP-6101 | DCS | INTERLOCK ACTIVATED FOR COMP. A |  |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 11 | OFF-PULSE | ON-PULSE
ULT003 - PLC I/O LIST COUNT IS PER UNIT
|  | AI : Analog Input AO : Analog Input H : Hardwire S : Serial DI: Digital Input DO: Digital Output DCS : Data Control Center MCC : Motor Control Center UCP-6101 : Unit Control Panel LCP : Local Control Station PLC : Programmable Logic Controller PW400 : POWER SUPPLY 400 W This IO List is a document containing list of instrumentation which serve as input or output of control system. | [5 empty] | AIR: Analog Input Redundancy AOR: Analog Output Redundancy DIR: Digital Input Redundancy DOR: Digital Output Redundancy NO: Normally Open NC: Normally Close NDE: Normally De- Energize NE: Normally Energize
STATES
TAG |  | SERVICE | PID DWG No. |  | TYPE | FROM | TO | DESCRIPTION |  | Engineering units | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL | RELAY OUTPUT | POWER SUPPLY | TYPE | SERIAL | IS/NIS | RACK | SLOT | CHANNEL | STATES'0' | STATES'1'
Card Type: Digital IN/ 16
Card Type/: Analog IN/ 8
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- SUCTION PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 0
PT-61113 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- OIL SUPPLY PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 1
TT-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A-SUCTION TEMPERATURE |  | C | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 2
VT-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- CASING VIBRATION |  | G | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 3
ZT-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- SLIDE VALVE POSITION |  | % | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 4
[8 empty] | SPARE |  |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 8 | 5
TE/TT-61127 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -B- BEARING TEMP DE (Note 1) |  | C | COMP -B- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 6
TE/TT-61128 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -B- BEARING TEMP NDE (Note 1) |  | C | COMP -B- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 7
Card Type/: Analog IN/ 8
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- SUCTION PRESSURE |  | Bar | COMP SKID | JB-UIA-621 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 0
PT-61123 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- OIL SUPPLY PRESSURE |  | Bar | COMP SKID | JB-UIA-621 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 1
TT-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B-SUCTION TEMPERATURE |  | C | COMP SKID | JB-UIA-621 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 2
VT-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- CASING VIBRATION |  | G | COMP SKID | JB-UIA-61121 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 3
ZT-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- SLIDE VALVE POSITION |  | % | COMP SKID | JB-UIA-621 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 4
[8 empty] | SPARE |  |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 9 | 5
TE/TT-61117 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -A- BEARING TEMP DE (Note 1) |  | C | COMP -A- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 6
TE/TT-61118 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -A- BEARING TEMP NDE (Note 1) |  | C | COMP -A- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 7
Card Type/: Analog IN/ 8
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61131 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMMON DISCHARGE PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 0
PT-61132 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COALESCER ELEMENT OUTLET PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 1
PT-61133 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | OIL FILTER SUPPLY PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 2
PT-61134 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | OIL SUPPLY PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 3
TT-61131 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | OIL SEPARATOR TEMPERATURE |  | C | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 4
TT-61132 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | OIL SUPPLY TEMPERATURE |  | C | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 5
LT-61131 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | OIL SEPARATOR LEVEL |  | % | COMP SKID | JB-UIA-611 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 6
[8 empty] | SPARE |  |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 10 | 7
Card Type/: Analog IN/ 8
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
TIC-61101 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | DCS | UCP-6101 | CHILLER TUBE OUTLET TEMPERTURE |  | C | VESSELS SKID | JB-UIA-61141 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 0
LT-61151 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | CHILLER LEVEL |  | % | VESSELS SKID | JB-UIA-641 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 1
[8 empty] | SPARE |  |  |  |  | AI | 4-20mA | - | PW400 |  |  |  | 2 | 11 | 2
PT-61141 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | ECONOMIZER TUBESIDE PRESSURE |  | Bar | COMP SKID | JB-UIA-641 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 3
TT-61141 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | ECONOMIZER TUBESIDE TEMPERATURE |  | Bar | COMP SKID | JB-UIA-641 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 4
TT-61190 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | UCP-6101 | UCP-6101 | UNIT CONTROL PANEL TEMPERATURE |  | C | UCP-6101 | UCP-6101 | AI | 4-20mA | - | PW400 | H | S | NIS | 2 | 11 | 5
IT-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | MCC | UCP-6101 | COMPRESSOR -A- MOTOR CURRENT |  | AMPS | MCC | UCP-6101 | AI | 4-20mA | - | PW400 | H | S | NIS | 2 | 11 | 6
IT-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | MCC | UCP-6102 | COMPRESSOR -B- MOTOR CURRENT |  | AMPS | MCC | UCP-6101 | AI | 4-20mA | - | PW400 | H | S | NIS | 2 | 11 | 7
Card Type/: Analog IN/ 8
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61111 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- SUCTION PRESSURE |  | Bar | COMP SKID | JB-UIA-611 | AIR | 4-20mA | - | PW400 | H | S | IS | 2 | 12,13 | 0
PT-61121 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- SUCTION PRESSURE |  | Bar | COMP SKID | JB-UIA-621 | AIR | 4-20mA | - | PW400 | H | S | IS | 2 | 12,13 | 1
LT-61131 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | OIL SEPARATOR LEVEL |  | % | COMP SKID | JB-UIA-611 | AIR | 4-20mA | - | PW400 | H | S | IS | 2 | 12,13 | 2
LT-61151 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | FIELD | UCP-6101 | CHILLER LEVEL |  | % | VESSELS SKID | JB-UIA-641 | AIR | 4-20mA | - | PW400 | H | S | IS | 2 | 12,13 | 3
[8 empty] | SPARE | [11 empty] | 2 | 12,13 | 4
[8 empty] | SPARE | [11 empty] | 2 | 12,13 | 5
[8 empty] | SPARE | [11 empty] | 2 | 12,13 | 6
[8 empty] | SPARE | [11 empty] | 2 | 12,13 | 7
Card Type: Analog OUT 4
TAG | [7 empty] | DESCRIPTION |  |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PV-61151 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | UCP-6101 | FIELD | HOT GAS BYPASS CONTROL VALVE |  | % | VESSELS SKID | JB-UIA-641 | AOR | 4-20 mA | - | - | H | S | IS | 2 | 14,15 | 0
LV-61151 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | UCP-6101 | FIELD | CHILLER LEVEL CONTROL VALVE |  | % | VESSELS SKID | JB-UIA-641 | AOR | 4-20 mA | - | - | H | S | IS | 2 | 14,15 | 1
TV-61141 |  | Propylene | VD-GPIC-MA-3029-3029-0015 |  | FLOAT/REAL | UCP-6102 | FIELD | ECONOMIZER TEMPERATURE CONTROL VALVE |  | % | VESSELS SKID | JB-UIA-641 | AOR | 4-20 mA | - | - | H | S | IS | 2 | 14,15 | 2
[8 empty] | SPARE |  |  |  |  | AOR | 4-20 mA |  | - |  |  |  | 2 | 14,15 | 3
Note (1)- Barrier converter installed in UCP to convert PT100 Signal to 4-20mA signal