## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Inter- en aftercooler datasheet | 17735-11B
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  | 2 | Closed | Discrepancy with PID to be removed | Discrepancy will be filled in the PID. The values in these datsheet are correct | Noted, utility consumption to be revised | noted
2 |  | 2 | Closed | ASTM No. And grade of all materials to be mentioned | Added material grades according to latest revision of cooler drawings | Check comments on data sheet. | noted
3 |  | 3 | Closed | 1- For design pressures please write from -1 bar(g) or vacum to ... bar(g). For design temperature also mention the lower bound. 2- All discrepancy with approved drawing to be revised. 3- add volume and hydrostatic test pressure of shell and tube side. | We keep our documents with the same data. We use the design pressure / temperature defined in the P&ID for this project. This is also commented from your side. For example 30 * 1.3 = 39 bar design pressure. So design data will stay the same as defined. actual or tested can be higher, but never lower.
4 |  | 3 | Closed | -1 to 39 bar(g) as per approved drawing. For de3sign temperature -10/175 C. | noted
5 |  | 3 | Closed | -1 to 10 bar(g) as per approved drawing. for design temperature -10/100 C. | noted
6 |  | 3 | Closed | please recheck by approved drawing and revise. material seems to be SA-240. | The main material (Shell and tube) is SA-312 as indicated on the latest drawing.
7 |  | 3 | Closed | Add operating weight as well. | Updated |  |  |  | Open
8 |  | 4 | Closed | Outlet pressure of 2nd stage compressor is equal to 30 barg, considering 0.94 bar as pressure drop of after cooler, air pressure at BL will be almost 29 barg (line loss is ignored) that has discrepancy with reported value in vendor P&ID and compressor data sheet. Also, this issue already has been commented in compressor data sheet, that 30 barg is required in package BL and compressor discharge pressure shall be calculated considering pressure drop from package BL to compressor nozzle. | Please note that the differential pressure is in mbar and not in bar. Differential pressure of 0,94 mbar -> 0,00094 bar is negligible. |  |  |  | Closed
9
10
11
12
13
14
15
16
17
18
19
20