## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Earthing diagram CRS | 17735-41
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 3 | 1 | Open | For Devices with voltage less than 50 VDC which their body have bonding to pipe/equipment via process connection no need to earth connection of cable armor and device body in instrument side. | The transmitters have an external earth connection connected to an earthing point, which is why it is drawn here. This earthing is not through the cable. The cable armor is not earthed on the instrument side. | Noted.
2
3
4
5
6
7 | [8 empty] | Open
8 | [8 empty] | Closed
9
10
11
12
13
14
15
16
17
18
19
20