## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 27/Oct/2021 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: Instrument Datasheets for Emergency Instrument air compressor
|  | Transmittal No.: APCES-V-00042 | Doc. No.: BU-20-VD-303-IN-DSH-0090
|  | Transmittal Date: 27/10/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
2 | General comment for all PG/PDG gauges shall be provided with zero stop pin and zero adjustable mechanis, shall be provided. |  |  | Updated in next revision |  |  | Closed.
3 | Ambient / 45°C |  |  | Updated in next revision |  |  | Closed.
4 | As per project specification PDG connection shall be 1/2" NPT |  |  | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors. |  |  | Closed.
5 | Instrument Air |  |  | Updated in next revision |  |  | Closed.
6 | 0-40 standard range to be considered |  |  | Updated in next revision |  |  | Closed.
7 | Bar (g) |  |  | All other pressures in process and scales are indicated with bar(a) |  |  | Closed.
8 | Gauges with maximum scale value of 25 bar g and more shall be solid front |  |  | Updated in next revision |  |  | Closed.
9 | Please be informed that pipe to be expanded to 4" for installation of TW on pipe |  |  | Noted, however line number as per P&ID. |  |  | Closed.
10 | Stem orientation shall be every angle. |  |  | This is for fieldmounted gauges, not fpr panel mounted. |  |  | Closed.
11 | 10004/ 10002; based on based on vendor PID |  |  | Not clear what you mean please clarify. |  |  | There is no such a comment
12 | U-length shall be specified by Airpack so that with considering TW tip stai on the middle third of pipe. |  |  | Updated in next revision |  |  | Please specify TW nozzle projection. it seems that selected U-length is too short to TW tip stay on the middle third of pipe.
13 | Airpack shall submit wake frequency calculations sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | This has not been agreed upon in the contract. |  |  | Please attach related MOM or TCL about this agreement.
14 | XY-10002 is one of the XV-10002 accessories it shall be removed and mentioned in On-off valve datasheet. |  |  | As it has a separate Tag number a seperated dataheet has been incorporated and not only an accessorie of valves. |  |  | Solenoid valve shall has a separate tag no. but it is one of the XV-71102 accessories and must be mentioned in on-off valve data sheet and removed from this data sheet.
15
16
17
18
19
20
21
22