## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 16/Nov/2021 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT HOOK UP DRAWING FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00051 | Doc. No.: BU-20-VD-303-IN-DWG-0033
|  | Transmittal Date: 16/Nov/2021 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | Drawing shall be match the title of the project title block |  |  | Noted. |  |  | Noted.
2 | Summary BOM table shall be prepared. Items code no. shall be unique. |  |  | BOM table for each instrument is provided in the drawing. Summary BOM will not be provided. |  |  | Noted.
3 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | Noted. |  |  | Noted.
4 | For process connection refer to comments on data sheet. |  |  | For PDG 1/4" is standard connection, 1/2" not available. |  |  | Noted.
5 | to be corrected to 1/2" |  |  | It will be updated accordingly. |  |  | Noted.
6 | general comment: tag names to be corrected as per PID. |  |  | Noted. Tag numbers will be updated. |  |  | Noted.
7 | Please note attached hook up of project and correct all items accordingly. |  |  | Noted. The attached file will be taken as a reference. |  |  | Noted.
8 | general comment: tube and cap to be considered for drain /vent of manifold. |  |  | Noted. It will be incorporated. |  |  | Noted.
9 | IN |  |  | Noted. It will be incorporated. |  |  | Noted.
10 | PI |  |  | Noted. It will be incorporated. |  |  | Noted.
11 | general comment: piping/instrument battery limit to be indicated.(in this doc only inst items to be mentioned in BOM table and related items of piping department to be mentioned in other docs) |  |  | Noted. It will be incorporated. |  |  | Noted.
12 | QTY of all instruments to be in accordance with PID and data sheet. |  |  | Noted. It will be incorporated. |  |  | Noted.
13 | trasnmitter |  |  | Noted. It will be incorporated. |  |  | Noted.
14 | this part is as internal part of valve and 1 integrated on / off valve including ball valve and related SOV will be supplied by vendor. But related instrument air tubing to be indicated in hook up from main header of inst air. |  |  | Intrument air air tubing is already shown. But from main header will be shown as "FROM COM. INLET". |  |  | Required connections to be specified in hook-up.
15 | Related instrument air tubing to be indicated in hook up from main header of inst air. |  |  | Intrument air air tubing is already shown. But from main header will be shown as "FROM COM. INLET". |  |  | Please refer to attached file about air hook-up in the document.