## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 10/Dec/2021 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT CABLE LIST & SHEDULE FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00067 | Doc. No.: BU-20-VD-303-IN-LST-0038
|  | Transmittal Date: 10/Dec/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | Cables numbering procedure, cable type, gland size, number of pair/core and sheath color shall be as per attached file. Numbering of single pair cables is the same as instrument tag numbers. |  |  | For internal cables the numbering procedure will not be followed. Cable tag numbers are according to per wiring diagram. |  |  | Closed. Also please mention multi cable numbering procedure and cable code in general note.
2 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | Noted. It will be incorporated. |  |  | Closed.
3 | cable specification to be added for each cable. ARM./ UNAR SHEATH /color PROTECTION (IS/NIS) CABLE LAYERS … |  |  | Noted. Cable information such as arm/unarm, sheath color, protection and cable type will be added. |  |  | Closed.
4 | cable length to be added for each item except customer scope of supply . |  |  | The cables are internal cables, so the length will not be indicated. |  |  | Closed. Please review and modify scope column.
5 | FOR CABLE TAG PLEASE NOTE ATTACHED NUMBERING PROCEDURE. |  |  | For internal cables the numbering procedure will not be followed. Cable tag numbers are according to per wiring diagram. |  |  | Cable list and also wiring diagram shall follow project numbering procedure.
6 | Gland size to be selected as per attache file. |  |  | Noted. It will be incorporated. |  |  | Closed.
7 | AO signal to be connected to analogue JB |  |  | Noted. It will be incorporated. |  |  | Closed.
8 | signals between MCC and LCP/PLC to be corrected as per project PID. |  |  | Noted. It will be udpated according to per P&ID. |  |  | Closed.
9 | Multi cable numbering procedure and cable code that was sent in previous revision of this document shall be mentioned in general note. |  |  | Noted. It will be incorporated. |  |  | Closed.
10 | To be review and modified the scope. |  |  | Noted. It will be incorporated. |  |  | Closed.
11 | ESD command is from customer ESD system to UCP not LCP Please modify in this document and also wiring diagram Please consider one 5pair cable between ESD system and UCP (for shut down command and trip status) |  |  | Noted. It will be incorporated. |  |  | Closed.
12 | For the cable ICNDX-C1002-FCS consider 1Px0,75. |  |  | Consider 2Px0,75mm² , because of aditional signals. |  |  | Please refer to comment on the document.
13 | For the cable FCNDX-C1002-LCP02 consider 10Px0,75 mm² |  |  | Noted. It will be incorporated. But pointed out that some spare IOs will not be wired. |  |  | Noted, please refer to modification for terminal strip X5 and X9 on wiring diagram.