## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 06/DEC/2021 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: CAUSE & EFFECT CHART LIST FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00063 | Doc. No.: BU-20-VD-303-PR-LST-0042
|  | Transmittal Date: 06/DEC/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | - Reply sheet to be submitted by vendor. - Prerequisite documents such as I/O List shall be sent before this document. - Tag no. to be revised as per comments on PID. - following signals to be considered in C&E : • C-1002-MOS-1 • HS-108-1R-1 |  |  | -Noted - Have been submitted - Noted has ben revised - as previously discussed this is not required |  |  | Closed.
2 | This signal is not required |  |  | Noted and removed |  |  | Closed.
3 | XAL-108-2 |  |  | Noted and updated |  |  | Closed.
4 | XAL-108-2 is trip status signal to client ESD system and it shall be separate from "Common Alarm To DCS" "Common Alarm To DCS" can be send to DCS via serial link connection accordingly all specified green boxes to be modified. |  |  | Noted and updated |  |  | Closed.
5 | ESD |  |  | Noted and updated |  |  | Closed.