## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 09/Jun/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: I/O LIST FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00145 | Doc. No.: BU-20-VD-303-IN-LST-0084
|  | Transmittal Date: 09/Jun/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | PB-71103 on local panel, for compressor ESD PB is missed in I/O list. Please clarify about HM-71101 signal, why are you considering a light for hourmeter? what does this light do? |  |  | ESD button on LP will be added. HM is hourmeter, without light. The instrument type will be adjusted. |  |  | Noted.
2 | P&ID number to be modified as per related P&ID document number. |  |  | Noted. It will be incorporated. |  |  | Noted.
3 | Nitrogen" to be modified to "Air" Please modify other description if required |  |  | Noted. It will be incorporated. |  |  | Noted.
4 | (Unload/Stop) |  |  | Noted. It will be incorporated. |  |  | Noted.
5 | To be specified |  |  | Noted. It will be incorporated. |  |  | Noted.
6 | Please modify to "-" |  |  | Noted. It will be incorporated. |  |  | Noted.
7 | State 0 must be Off/Local |  |  | Noted. It will be incorporated. |  |  | Noted.
8 | State 1 must be Remote only |  |  | Noted. It will be incorporated. |  |  | Noted.
9 | Tag no. shall be specified |  |  | Please advise the tag numbers. |  |  | Noted.
10 | FCS |  |  | Noted. It will be incorporated. |  |  | Noted.
11 | - Signal for PY-71101 is missed - Please add I/O summary table for each I/O type. |  |  | Noted. It will be incorporated. |  |  | Noted.
12 | Please fill xx as your sequence HS-711xx-R HS-711xx-SD XS-711xx-ST/SP XS-711xx-ST/SP XL-711xx YAL-711xx XL-711xx YAL-711xx |  |  | Noted. It will be incorporated. |  |  | Noted.
| .- AO signal type shall be added. - I/O redundancy shall be mentioned |  |  | AO signals is through PID controller I/O reduncacy is mentioned already |  |  | - AO card for control valve must be considered, PID controller is not accepted. - Closed.
| 18/16 |  |  | Noted. It will be incorporated. |  |  | Closed.
| According to existing PLC in your UCP, so PID controller is not accepted and AO card must be considered, and also PID controller has conflict with issued P&ID, in the P&ID, control valve has been controlled via UCP. Please consider one analogue output card to control control valve, with considering related pressure signal that coming to UCP. |  |  | There is no specification that an PID controller is not allowed, Airpack has used this in all project in the past. And we cannot deviate from this as this is part of our control |  |  | With considering that this is not a normal design, but it is accepted with vendor guarantee, also vendor shall consider at least one PID controller with same specification in spare part list.
| Please refer to comment in previous page |  |  | There is no specification that an PID controller is not allowed, Airpack has used this in all project in the past. And we cannot deviate from this as this is part of our control