## IO_Summary
I/O SUMMARY for POWDER Transfer Package
PROJECT : 300 KT POLYETHYLENE PLANT ARYA SASOL POLYMER COMPANY (ASPC)
DESCRIPTION |  | DI | DO | AI | AO | PI | SUM | REMARK
| POWDER (DCS) | 8 | 6 | 8 | 3 | 2 | 27
| POWDER (ESD) | 4 | 6 | 6 | 0 | 0 | 16
TOTAL |  | 12 | 12 | 14 | 3 | 2 | 43
Note.
* It's actual I/O points. The DCS/ESD System has to have 20% spare points.

## GUIDE-I
DESCRIPTION and USER'S GUIDE for IO LIST
1. General Notes
1) This list applies to measurements and devices to be monitored and controlled by the DCS.
2) For preparing the measurement List, the following format and description are to be used as guide-lines.
2. Format and guide-lines to fill out
|  | NO |  |  |  | TAG NO |  | SERVICE DESCRIPTION | FROM /TO | SIGNAL TYPE |  | PWR SRC |  | I/O TYPE | CONT -ACT | FUNCTION | [5 empty] | INST TYPE | IS/NIS | VALVE ACTION | LOOP TAG NO | JUNCTION BOX NO | P & ID NO. | LOGIC NO. | REVISION HISTORY | REMARK
[16 empty] | C | I | R | A | Z | SOE
|  | (1) |  |  |  | (2) |  | (3) | (4) | (8) |  | (9) |  | (10) | (11) | (12) | [5 empty] | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
(1) NO : Serial Number
(2) TAG NO : Identification Number (20 digits with dash mark)
(3) SERVICE DESCRIPTION
Service description of instrument or device is specified.
(4) FROM/TO (5 digits)
"FROM" means the source of DCS input signal and "TO" means the destination of DCS output signal as follows ;
[5 empty] | FLD |  | : FIELD (OR LOCAL) |  |  |  | BC |  | : BATTERY CHARGER
[5 empty] | MCC |  | : MOTOR CONTROL CENTER |  |  |  | DG |  | : DIESEL GENERATOR
[5 empty] | SG |  | : SWITCHGEAR |  |  |  | PRP |  | : PROTECTION RELAY PANEL
[5 empty] | LC |  | : LOAD CENTER |  |  |  | TDP |  | : TRANSDUCER PANEL
[5 empty] | CCB |  | : CENTRAL CONTROL BUILDING |  |  |  | TPP |  | : T/L PROTECTION PANEL
[5 empty] | LCP |  | : LOCAL CONTROL PANEL |  |  |  | BFP |  | : BREAKER FAILURE PANEL
[5 empty] | EPLC |  | : ELECTRIC PROGRAMMABLE LOGIC CONTROLLER
[5 empty] | BPP |  | : BUS PROTECTION PANEL |  |  |  | DP |  | : DISTRIBUTION PANEL
[5 empty] | UPS |  | : UNINTERRUPTIBLE POWER SYSTEM |  |  |  | VR |  | : VOLTAGE REGULATOR SYSTEM
[5 empty] | ANN |  | : PLANT ANNUNCIATOR SYSTEM |  |  |  | COAL |  | : COAL HANDLING SYSEM
[5 empty] | ELE |  | : ELECTRICAL AUX RELAY |  |  |  | DCS |  | : DISTRIBUTED CONTROL SYSTEM
[5 empty] | VMS |  | : VIBRATION MONITORING SYSTEM |  |  |  | ESD |  | : EMERGENCY SHUTDOWN
[5 empty] | ECMS |  | : ELECTICAL CONTROL AND MONITORING SYSTEM
[5 empty] | PTC |  | : PULSE TIMER CONTROLLER |  |  |  | MCC-VFD |  | : Variable frequency drive located in substation
[5 empty] | LCS |  | : LOCAL CONTROL STATION |  |  |  | RLY |  | : INTERPOSING RELAY CABINET
(5) RANGE (20 digits)
Process variable range is specified.(for example 300 ~ 10,000)
(6) UNIT (8 digits)
The engineering units used in this list are as follows ;
[7 empty] | ORIGINAL UNIT |  | DESCRIPTION USED |  |  |  | ORIGINAL UNIT |  |  | DESCRIPTION USED
[7 empty] | bar gage |  | bar.g (mbar.g) |  |  |  | Megawatt |  |  | MW
[7 empty] | Vacuum |  | mbar.a |  |  |  | Hertz |  |  | Hz, KHz
[7 empty] | ℃ (Degree C) |  | ℃ |  |  |  | Percent |  |  | %
[7 empty] | millimeter, inch |  | MM, IN |  |  |  | micro mho/Cm |  |  | UMHO
[7 empty] | Meter |  | M |  |  |  | kcal/hour |  |  | KC/H
[7 empty] | part(s) per million |  | PPM |  |  |  | revolution per minute |  |  | RPM
[7 empty] | part(s) per billion |  | PPB |  |  |  | Ton/Hour |  |  | T/H
[7 empty] | pH |  | PH |  |  |  | kg/hour |  |  | KG/H
[7 empty] | Volt |  | V |  |  |  | liter/minute |  |  | L/M
[7 empty] | Kilovolt |  | KV
[7 empty] | Ampere |  | A
(7) SET POINT
This column shows the software threshold value in analog input for alarm or interlock purpose.
- HH : High-High Alarming
- H : High Alarming
- L : Low Alarming
- LL : Low-Low Alarming
(8) SIGNAL TYPE (6 digits)
The type of input/output signal is specified as follows ;
|  |  |  | 4~20mA |  |  | : 4-20 mA with HART protocol
|  |  |  | NAMUR |  |  | : NAMUR for proximity switches
|  |  |  | 24V DC |  |  | : 24V DC binary signals
|  |  |  | VFC |  |  | : Volt Free Contact
(9) PWR SRC : Power source (1 digit)
The power source of signal is specified as follows ;
|  |  |  | . I |  |  | : INTERNAL POWER SUPPLIED FROM DCS
|  |  |  | . E |  |  | : EXTERNAL POWER SUPPLIED FROM OUTSIDE OF DCS
(10) I/O TYPE ( 2 digits)
The signal type of input or output is specified as follows :
|  |  |  | . AI |  |  | : ANALOG INPUT
|  |  |  | . AO |  |  | : ANALOG OUTPUT
|  |  |  | . DI |  |  | : DIGITAL INPUT
|  |  |  | . DO |  |  | : DIGITAL OUTPUT
|  |  |  | . DO | PI |  | : PULSE INPUT
(11) CONTACT : Contact type (2 digits)
The status of digital contact is specified when the equipment is de-energized, closed or stopped etc.
|  |  |  | . NO |  |  | : NORMALLY OPEN CONTACT
|  |  |  | . NC |  |  | : NORMALLY CLOSED CONTACT
(12) FUNCTION
The function of I/O Signal is marked in appropriate column. This column shows variable function displayed on LED of DCS.
The Function on this column refers as follows;
- C : Controlling
- I : Indicating
- R : Recording or Trending
- A : Alarm
- Z : Plant Protection
- SOE : Sequence of Event
(13) INST TYPE
The description of Tag No.
(14) IS/NIS
The Ex. Protection types
(15) VALVE ACTION
Valve PID action (Direct / Reverse) is specified.
(16) LOOP TAG NO.
Loop tag number is specified.
(17) JUNCTION BOX NO.
Junction box number is specified.
(18) P & ID NO.
P&ID drawing number is specified.
(19) LOGIC NO.
Logic/Loop drawing number is specified.
(20) REVISION HISTORY
Revision history is specified.
(21) REMARK
Additional information is described.

## Powder_IO (DCS)
[10 empty] | PROJECT NO. : 3944 | IO LIST (DCS) FOR POWDER TRANSFER PACKAGE
MR NO. : 171
DOC TITLE : IO LIST (POWDER)
DOC NO. : 3944-VD-0171-DYP-RE-400-LST-0080
REV : 02
| NO | TAG NO. | [6 empty] | TAG NO. | SERVICE DESCRIPTION | FROM /TO | RANGE | UNIT | SET-POINT |  |  |  | SIGNAL TYPE | PWR SRC | I/O TYPE | CONT -ACT | FUNCTION | [5 empty] | INST TYPE | IS / NIS | VALVE ACTION | LOOP TAG NO. | JUNCTION BOX NO. | P&ID NO. (3944-VD-0171-DYP-RE-400-PID-0016 Rev.02) | LOGIC NO. (3944-VD-0171-DYP-RE-400-DIA-0083 Sh.NNN) | REVISION HISTORY | REMARK | DI | DO | AI | AO | PI | SUM
for Sort | [13 empty] | LL | L | H | HH |  |  |  |  | C | I | R | A | Z | SOE | [9 empty] | 8 | 6 | 8 | 3 | 2 | 27
- | Instruments
- | 1 | 44 | FT | - | 20070 | 60 |  |  | 44FT-2007060 | POWDER CONVEYING N2 SUPPLY FLOW | FLD / DCS | 0~600 | Nm3/h | - | 450 | - | - | 4~20mA | I | AI | - |  | O |  | O |  |  | FLOW TRANSMITTER DP-INTEGRAL ORIFICE | IS | - | by other | by other | 20070 | 072
- | 2 | 44 | PT | - | 20070 | 62 |  |  | 44PT-2007062 | POWDER CONVEYING N2 SUPPLY PRESSURE | FLD / DCS | 0~6 | bar.g | 3 | 3.5 | 4.5 | 5 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 073
- | 3 | 44 | PT | - | 20070 | 19 |  |  | 44PT-2007019 | 44Z-20002A CONVEYING STATION PURGING PRESSURE | FLD / DCS | 0~5 | bar.g | - | 1.8 | - | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 082
- | 4 | 44 | PT | - | 20070 | 20 |  |  | 44PT-2007020 | 44Z-20002B CONVEYING STATION PURGING PRESSURE | FLD / DCS | 0~5 | bar.g | - | 1.8 | - | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 087
- | 5 | 44 | PDT | - | 20070 | 03 |  |  | 44PDT-2007003 | 44F-20002 VENT FILTER DIFF. PRESSURE | FLD / DCS | 0~500 | mmH2O | - | - | 300 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | DIFF PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 099
- | 6 | 44 | LSH | - | 20070 | 03A |  |  | 44LSH-2007003A | 44V-20001A BLOW TANK LEVEL HIGH SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH HIGH | IS | - | by other | by other | 20070 | 098
- | 7 | 44 | LSL | - | 20070 | 02A |  |  | 44LSL-2007002A | 44V-20001A BLOW TANK LEVEL LOW SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH LOW | IS | - | by other | by other | 20070 | 098
- | 8 | 44 | LSH | - | 20070 | 03B |  |  | 44LSH-2007003B | 44V-20001B BLOW TANK LEVEL HIGH SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH HIGH | IS | - | by other | by other | 20070 | 098
- | 9 | 44 | LSL | - | 20070 | 02B |  |  | 44LSL-2007002B | 44V-20001B BLOW TANK LEVEL LOW SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH LOW | IS | - | by other | by other | 20070 | 098
- | 10 | 44 | PDT | - | 40000 | 03 |  |  | 44PDT-4000003 | 44F-40002A VENT FILTER DIFF. PRESSURE | FLD / DCS | 0~500 | mmH2O | - | - | 300 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | DIFF PRESSURE TRANSMITTER | IS | - | by other | by other | 40000 | 123
-
- | Valves
XV-2007005 | 1 | 44 | XVYA | - | 20070 | 05 |  |  | 44XVYA-2007005 | POWDER CONVEYING N2 SUPPLY VALVE OPEN COMMAND | DCS / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | FAIL CLOSE | by other | by other | 20070 | 071
XV-2007005 | 1 | 44 | XVYB | - | 20070 | 05 |  |  | 44XVYB-2007005 | POWDER CONVEYING N2 SUPPLY VALVE OPEN COMMAND | DCS / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | - | by other | by other | 20070 | 071 | Added in Revision.02
XV-2007005 | 2 | 44 | ZSH | - | 20070 | 05 |  |  | 44ZSH-2007005 | POWDER CONVEYING N2 SUPPLY VALVE OPEN LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | 071
XV-2007005 | 3 | 44 | ZSL | - | 20070 | 05 |  |  | 44ZSL-2007005 | POWDER CONVEYING N2 SUPPLY VALVE CLOSE LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | 071
FV-2007060 | 4 | 44 | FVGC | - | 20070 | 60 |  |  | 44FVGC-2007060 | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE DEMAND | DCS / FLD | 0~100 | % | - | - | - | - | 4~20mA | I | AO | - | O | [5 empty] | POSITIONER | IS | REVERSE | by other | by other | 20070 | 072
FV-2007060 | 5 | 44 | FZLH | - | 20070 | 60 |  |  | 44FZLH-2007060 | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE OPEN LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI(x) | NO |  | O |  |  |  |  | - | - | - | - | - | 20070 | LATER | Deleted in Revision.01
FV-2007060 | 6 | 44 | FZLL | - | 20070 | 60 |  |  | 44FZLL-2007060 | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE CLOSE LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI(x) | NO |  | O |  |  |  |  | - | - | - | - | - | 20070 | LATER | Deleted in Revision.01
XV-2007001 | 7 | 44 | XVYA | - | 20070 | 01 |  |  | 44XVYA-2007001 | 44TK-20001A INLET KNIFE GATE OPEN COMMAND | DCS / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | FAIL LAST | by other | by other | 20070 | 011
XV-2007001 | 8 | 44 | XVYB | - | 20070 | 01 |  |  | 44XVYB-2007001 | 44TK-20001A INLET KNIFE GATE CLOSE COMMAND | DCS / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | FAIL LAST | by other | by other | 20070 | 011
XV-2007001 | 9 | 44 | ZSH | - | 20070 | 01 |  |  | 44ZSH-2007001 | 44TK-20001A INLET KNIFE GATE OPEN LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL LAST | by other | by other | 20070 | 011
XV-2007001 | 10 | 44 | ZSL | - | 20070 | 01 |  |  | 44ZSL-2007001 | 44TK-20001A INLET KNIFE GATE CLOSE LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL LAST | by other | by other | 20070 | 011
-
- | Motor, Others
44Z-20002A | 1 | 44 | SIC | - | 20070 | 19A |  |  | 44SIC-2007019A | 44Z-20002A CONVEYING STATION SPEED CONTROLLER | DCS / MCC-VFD | 0~19.4 | RPM | - | - | - | - | 4~20mA | I | AO | - | O | [5 empty] | MOTOR SPEED DEMAND | NIS | - | by other | by other | 20070 | 082
44Z-20002A | 2 | 44 | SI | - | 20070 | 19A |  |  | 44SI-2007019A | 44Z-20002A CONVEYING STATION SPEED FEEDBACK | MCC-VFD / DCS | 0~19.4 | RPM | - | - | - | - | 4~20mA | I | AI | - |  | O |  |  |  |  | MOTOR SPEED FEEDBACK | NIS | - | by other | by other | 20070 | 082
44Z-20002A | 3 | 44 | SE | - | 20070 | 01 |  |  | 44SE-2007001 | 44Z-20002A CONVEYING STATION SPEED SENSOR | FLD / DCS | - | - | - | - | - | - | NAMUR | I | PI | - |  | O |  | O |  |  | MOTOR SPEED SENSOR | NIS | - | by other | by other | 20070 | 081
44Z-20002A | 4 | 44 | Y | - | 20070 | 19A | - | FS | 44Y-2007019A-FS | 44Z-20002A CONVEYING STATION FAULT STATUS | EPLC / DCS | - | - | - | - | - | - | 24V DC | I | DI(X) | NO |  | O |  | O |  |  | MOTOR FAULT STATUS | NIS | - | by other | by other | 20070 | 081 | Deleted in Revision.02
44Z-20002A | 5 | 44 | Y | - | 20070 | 19A | - | PS | 44Y-2007019A-PS | 44Z-20002A CONVEYING STATION STOP COMMAND | DCS / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP COMMAND | NIS | - | by other | by other | 20070 | 081 | Added inRevision.2
44Z-20002B | 6 | 44 | SIC | - | 20070 | 19B |  |  | 44SIC-2007019B | 44Z-20002B CONVEYING STATION SPEED CONTROLLER | DCS / MCC-VFD | 0~19.4 | RPM | - | - | - | - | 4~20mA | I | AO | - | O | [5 empty] | MOTOR SPEED DEMAND | NIS | - | by other | by other | 20070 | 087
44Z-20002B | 7 | 44 | SI | - | 20070 | 19B |  |  | 44SI-2007019B | 44Z-20002B CONVEYING STATION SPEED FEEDBACK | MCC-VFD / DCS | 0~19.4 | RPM | - | - | - | - | 4~20mA | I | AI | - |  | O |  |  |  |  | MOTOR SPEED FEEDBACK | NIS | - | by other | by other | 20070 | 087
44Z-20002B | 8 | 44 | SE | - | 20070 | 02 |  |  | 44SE-2007002 | 44Z-20002B CONVEYING STATION SPEED SENSOR | FLD / DCS | - | - | - | - | - | - | NAMUR | I | PI | - |  | O |  | O |  |  | MOTOR SPEED SENSOR | NIS | - | by other | by other | 20070 | 086
44Z-20002B | 9 | 44 | Y | - | 20070 | 19B | - | FS | 44Y-2007019B-FS | 44Z-20002B CONVEYING STATION FAULT STATUS | EPLC / DCS | - | - | - | - | - | - | 24V DC | I | DI(X) | NO |  | O |  | O |  |  | MOTOR FAULT STATUS | NIS | - | by other | by other | 20070 | 086 | Deleted in Revision.02
44Z-20002B | 10 | 44 | Y | - | 20070 | 19B | - | PS | 44Y-2007019B-PS | 44Z-20002B CONVEYING STATION STOP COMMAND | DCS / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP COMMAND | NIS | - | by other | by other | 20070 | 086 | Added in Revision.02

## Powder_IO (ESD)
[10 empty] | PROJECT NO. : 3944 | IO LIST (ESD) FOR POWDER TRANSFER PACKAGE
MR NO. : 171
DOC TITLE : IO LIST (POWDER)
DOC NO. : 3944-VD-0171-DYP-RE-400-LST-0080
REV : 02
| NO | TAG NO. | [6 empty] | TAG NO. | SERVICE DESCRIPTION | FROM /TO | RANGE | UNIT | SET-POINT |  |  |  | SIGNAL TYPE | PWR SRC | I/O TYPE | CONT -ACT | FUNCTION | [5 empty] | INST TYPE | IS / NIS | VALVE ACTION | LOOP TAG NO. | JUNCTION BOX NO. | P&ID NO. (3944-VD-0171-DYP-RE-400-PID-0016 Rev.02) | LOGIC NO. (3944-VD-0171-DYP-RE-400-DIA-0083 Sh.NNN) | REVISION HISTORY | REMARK | DI | DO | AI | AO | PI | SUM
[14 empty] | LL | L | H | HH |  |  |  |  | C | I | R | A | Z | SOE | [9 empty] | 4 | 6 | 6 | 0 | 0 | 16
- | Instruments
- | 1 | 44 | PT | - | 20070 | 06A |  |  | 44PT-2007006A | 44V-20001A BLOW TANK PRESSURE-1 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | 7 | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 511
- | 2 | 44 | PT | - | 20070 | 07A |  |  | 44PT-2007007A | 44V-20001A BLOW TANK PRESSURE-2 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 511
- | 3 | 44 | PT | - | 20070 | 06B |  |  | 44PT-2007006B | 44V-20001B BLOW TANK PRESSURE-1 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | 7 | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 512
- | 4 | 44 | PT | - | 20070 | 07B |  |  | 44PT-2007007B | 44V-20001B BLOW TANK PRESSURE-2 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 512
- | 5 | 44 | PT | - | 20070 | 04 |  |  | 44PT-2007004 | POWDER TO 44R-20001 TRANSFER PRESSURE-1 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 513
- | 6 | 44 | PT | - | 20070 | 05 |  |  | 44PT-2007005 | POWDER TO 44R-20001 TRANSFER PRESSURE-2 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | 513
-
- | Valves
XV-2007017 | 1 | 44 | XVYA | - | 20070 | 17 |  |  | 44XVYA-2007017 | 44TK-20002A/B TO BLOW TANK VALVE-1 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | FAIL CLOSE | by other | by other | 20070 | 521
XV-2007017 | 2 | 44 | XVYB | - | 20070 | 17 |  |  | 44XVYB-2007017 | 44TK-20002A/B TO BLOW TANK VALVE-1 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | - | by other | by other | 20070 | 521 | Added in Revision.02
XV-2007017 | 3 | 44 | ZLSH | - | 20070 | 17 |  |  | 44ZLSH-2007017 | 44TK-20002A/B TO BLOW TANK VALVE-1 OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | 521
XV-2007017 | 4 | 44 | ZLSL | - | 20070 | 17 |  |  | 44ZLSL-2007017 | 44TK-20002A/B TO BLOW TANK VALVE-1 CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | 521
XV-2007014 | 5 | 44 | XVYA | - | 20070 | 14 |  |  | 44XVYA-2007014 | 44TK-20002A/B TO BLOW TANK VALVE-2 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | FAIL CLOSE | by other | by other | 20070 | 522
XV-2007014 | 6 | 44 | XVYB | - | 20070 | 14 |  |  | 44XVYB-2007014 | 44TK-20002A/B TO BLOW TANK VALVE-2 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | - | by other | by other | 20070 | 522 | Added in Revision.02
XV-2007014 | 7 | 44 | ZLSH | - | 20070 | 14 |  |  | 44ZLSH-2007014 | 44TK-20002A/B TO BLOW TANK VALVE-2 OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | 522
XV-2007014 | 8 | 44 | ZLSL | - | 20070 | 14 |  |  | 44ZLSL-2007014 | 44TK-20002A/B TO BLOW TANK VALVE-2 CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | 522
XV-2007042 | 9 | 44 | XVYA | - | 20070 | 42 |  |  | 44XVYA-2007042 | 44V-20001A BLOW TANK VENT FILTER VALVE OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | FAIL CLOSE | by other | by other | 20070 | 525
XV-2007042 | 10 | 44 | XVYB | - | 20070 | 42 |  |  | 44XVYB-2007042 | 44V-20001A BLOW TANK VENT FILTER VALVE OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | IS | - | by other | by other | 20070 | 525 | Added in Revision.02
-
- | Motors
- | 1 | 44 | Y | - | 20070 | 19A | - | ES | 44Y-2007019A-ES | 44Z-20002A CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 20070 | - | Deleted in Revision.02
- | 2 | 44 | Y | - | 20070 | 19B | - | ES | 44Y-2007019B-ES | 44Z-20002B CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 20070 | - | Deleted in Revision.02
- | 3 | 44 | Y | - | 40000 | 10A | - | ES | 44Y-4000010A-ES | 44Z-40001A CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40000 | - | Deleted in Revision.02
- | 4 | 44 | Y | - | 40000 | 10B | - | ES | 44Y-4000010B-ES | 44Z-40001B CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40000 | - | Deleted in Revision.02
- | 5 | 44 | Y | - | 40030 | 10A | - | ES | 44Y-4003010A-ES | 44Z-40002A ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40030 | - | Deleted in Revision.02
- | 6 | 44 | Y | - | 40030 | 11A | - | ES | 44Y-4003011A-ES | 44Z-40003A ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40030 | - | Deleted in Revision.02
- | 7 | 44 | Y | - | 40030 | 12A | - | ES | 44Y-4003012A-ES | 44Z-40004A ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40030 | - | Deleted in Revision.02
- | 8 | 44 | Y | - | 40040 | 10A | - | ES | 44Y-4004010A-ES | 44Z-40002B ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40040 | - | Deleted in Revision.02
- | 9 | 44 | Y | - | 40040 | 11A | - | ES | 44Y-4004011A-ES | 44Z-40003B ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40040 | - | Deleted in Revision.02
- | 10 | 44 | Y | - | 40040 | 12A | - | ES | 44Y-4004012A-ES | 44Z-40004B ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40040 | - | Deleted in Revision.02
- | 11 | 44 | Y | - | 50010 | 52 | - | ES | 44Y-5001052-ES | 44C-50008 EXHAUST FAN EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO(x) | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 50010 | - | Deleted in Revision.02