## ASPC(40001)
ELECTRICAL LOAD LIST
No. | Item No. | Description | Q'ty | Load Status |  |  | Load Type |  |  | Voltage | Phase | Freq | Rated Power | Shaft Power | Effic'y | PF | Remarks
|  |  |  | C | I | S | M | F | VFD | [V] | 1/3 | [hz] | [kW] | [kW] | [%] | [%]
Conveying Station / Rotary Valve
1 | 44Z-20002A-M1 | Conveying Station (12") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 2.2 | 1.32 | 86.7 | 68 | VFD
2 | 44Z-20002B-M1 | Conveying Station (12") | 1 |  | 1 |  |  |  | 1 | 400 | 3 | 50 | 2.2 | 1.32 | 86.7 | 68 | VFD
3 | 44Z-40001A-M1 | Conveying Station (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
4 | 44Z-40001B-M1 | Conveying Station (20") | 1 |  | 1 |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
5 | 44Z-40002A-M1 | Rotary Valve (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
6 | 44Z-40002B-M1 | Rotary Valve (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
7 | 44Z-40003A-M1 | Rotary Valve (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
8 | 44Z-40003B-M1 | Rotary Valve (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
9 | 44Z-40004A-M1 | Rotary Valve (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
10 | 44Z-40004B-M1 | Rotary Valve (20") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 7.5 | 6 | 90.4 | 85 | VFD
11 | 44Z-40001AM1-CS02 | Electric Heat Tracing for Conveying Station | - | 1 |  |  |  | 1 |  | 230 | 1 | 50 | 1.84 | - | - | -
12 | 44Z-40001BM1-CS02 | Electric Heat Tracing for Conveying Station | - |  | 1 |  |  | 1 |  | 230 | 1 | 50 | 1.84 | - | - | -
13
14 | Compressor
15 | 44C-40001A-M1 | Compressor Main Drive Motor | 1 | 1 |  |  | 1 |  |  | 6000 | 3 | 50 | 440 | 356 | Later | Later | Oil Pump Driven Through Gearbox
16 | 44C-40001A-M1-SH1 | Space Heater for Main Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
17 | 44C-40001A-M3 | Compressor Ventilation Fan Motor | 1 | 1 |  |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
18 | 44C-40001A-M2 | Oil Demister Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
19 | 44LCP-4001010 | Compressor LCP | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
20
21 | 44C-40001B-M1 | Compressor Main Drive Motor | 1 |  | 1 |  | 1 |  |  | 6000 | 3 | 50 | 440 | 356 | Later | Later | Oil Pump Driven Through Gearbox
22 | 44C-40001B-M1-SH1 | Space Heater for Main Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
23 | 44C-40001B-M3 | Compressor Ventilation Fan Motor | 1 |  | 1 |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
24 | 44C-40001B-M2 | Oil Demister Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
25 | 44LCP-4002010 | Compressor LCP | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
26
27 | Common
28 | 44WS-50001-M1 | Loading Device | 1 | 1 |  |  | 1 |  |  | 400 | 3 | 50 | 1.5 | 1 | 85.3 | 70
29 | 44C-50008-M1 | Exhaust Fan | 1 | 1 |  |  | 1 |  |  | 400 | 3 | 50 | 3.7 | 0.7 | 87.8 | 85
Note ; | 1. Legend ; M : Motor Type Feeder, F : Feed Type (Non Motor), VFD : Motor Type With VFD
2. Legend ; C : Continuous, I : Intermittent, S : Stand-by
1

## ASPC(80001,2,4,5)
ELECTRICAL LOAD LIST
No. | Item No. | Description | Q'ty | Load Status |  |  | Load Type |  |  | Voltage | Phase | Freq | Rated Power | Shaft Power | Effic'y | PF | Remarks
|  |  |  | C | I | S | M | F | VFD | [V] | 1/3 | [hz] | [kW] | [kW] | [%] | [%]
Conveying Station / Rotary Valve
1 | 44Z-50001A-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
2 | 44Z-50001B-M1 | Conveying Station (18") | 1 |  | 1 |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
3 | 44Z-80001A-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
4 | 44Z-80001B-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
5 | 44Z-80001C-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
6 | 44Z-80001D-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
7 | 44Z-80001E-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
8 | 44Z-80001F-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
9 | 44Z-80002A-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
10 | 44Z-80002B-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
11 | 44Z-80002C-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
12 | 44Z-80002D-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
13 | 44Z-80002E-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
14 | 44Z-80002F-M1 | Conveying Station (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 5.5 | 4.4 | 89.6 | 68 | VFD
15 | 44Z-80003A-M1 | Rotary Valve (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 3.75 | 2.25 | 88.4 | 68 | VFD
16 | 44Z-80003B-M1 | Rotary Valve (18") | 1 | 1 |  |  |  |  | 1 | 400 | 3 | 50 | 3.75 | 2.25 | 88.4 | 68 | VFD
17 | 44Z-80011-M1 | Rotary Valve (10") | 1 |  |  |  | 1 |  |  | 400 | 3 | 50 | 0.75 | 0.45 | 82.5 | 70 | DOL
18 | 44Z-80021-M1 | Rotary Valve (10") | 1 |  |  |  | 1 |  |  | 400 | 3 | 50 | 0.75 | 0.45 | 82.5 | 70 | DOL
19 | 44Z-80031-M1 | Rotary Valve (10") | 1 |  |  |  | 1 |  |  | 400 | 3 | 50 | 0.75 | 0.45 | 82.5 | 70 | DOL
20
21 | Compressor
22 | 44C-80001A-M1 | Compressor Main Drive Motor | 1 | 1 |  |  | 1 |  |  | 6000 | 3 | 50 | 250 | 196 | Later | Later | Oil Pump Driven Through Gearbox
23 | 44C-80001A-M1-SH1 | Space Heater for Main Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
24 | 44C-80001A-M3 | Compressor Ventilation Fan Motor | 1 | 1 |  |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
25 | 44C-80001A-M2 | Oil Demister Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
26 | 44LCP-8004011 | Compressor LCP | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
27
28 | 44C-80001B-M1 | Compressor Main Drive Motor | 1 |  | 1 |  | 1 |  |  | 6000 | 3 | 50 | 250 | 196 | Later | Later | Oil Pump Driven Through Gearbox
29 | 44C-80001B-M1-SH1 | Space Heater for Main Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
30 | 44C-80001B-M3 | Compressor Ventilation Fan Motor | 1 |  | 1 |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
31 | 44C-80001B-M2 | Oil Demister Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
32 | 44LCP-8004021 | Compressor LCP | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
33
34 | 44C-80002A-M1 | Roots Blower Main Drive Motor | 1 | 1 |  |  | 1 |  |  | 6000 | 3 | 50 | 250 | 193 | Later | Later | Ventilation Fan Driven Through V-Belt
35 | 44C-80002A-M1-SH1 | Space Heater for Main Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
36 | 44LCP-8004031 | Roots Blower LCP | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
37
38 | 44C-80002B-M1 | Roots Blower Main Drive Motor | 1 |  | 1 |  | 1 |  |  | 6000 | 3 | 50 | 250 | 193 | Later | Later | Ventilation Fan Driven Through V-Belt
39 | 44C-80002B-M1-SH1 | Space Heater for Main Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
40 | 44LCP-8004041 | Roots Blower LCP | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
41
42 | 44C-80004A-M1 | Compressor Main Drive Motor | 1 | 1 |  |  | 1 |  |  | 6000 | 3 | 50 | 560 | 479 | Later | Later | Ventilation Fan/Oil Pump Driven Through Gearbox
43 | 44C-80004A-M1-SH1 | Space Heater for Main Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
44 | 44C-80004A-M2 | Oil Demister Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
45 | 44LCP-8004051 | Compressor LCP | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
46
47 | 44C-80004B-M1 | Compressor Main Drive Motor | 1 |  | 1 |  | 1 |  |  | 6000 | 3 | 50 | 560 | 479 | Later | Later | Ventilation Fan/Oil Pump Driven Through Gearbox
48 | 44C-80004B-M1-SH1 | Space Heater for Main Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
49 | 44C-80004B-M2 | Oil Demister Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
50 | 44LCP-8004061 | Compressor LCP | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
51
52 | 44C-80005A-M1 | Compressor Main Drive Motor | 1 | 1 |  |  | 1 |  |  | 6000 | 3 | 50 | 250 | 197 | Later | Later | Oil Pump Driven Through Gearbox
53 | 44C-80005A-M1-SH1 | Space Heater for Main Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
54 | 44C-80005A-M3 | Compressor Ventilation Fan Motor | 1 | 1 |  |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
55 | 44C-80005A-M2 | Oil Demister Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
56 | 44LCP-8004071 | Compressor LCP | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
57
58 | 44C-80005B-M1 | Compressor Main Drive Motor | 1 | 1 |  |  | 1 |  |  | 6000 | 3 | 50 | 250 | 197 | Later | Later | Oil Pump Driven Through Gearbox
59 | 44C-80005B-M1-SH1 | Space Heater for Main Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.173 | 0.173 | Later | Later
60 | 44C-80005B-M3 | Compressor Ventilation Fan Motor | 1 | 1 |  |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
61 | 44C-80005B-M2 | Oil Demister Motor | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
62 | 44LCP-8004081 | Compressor LCP | 1 | 1 |  |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
63
64 | 44C-80005C-M1 | Compressor Main Drive Motor | 1 |  | 1 |  | 1 |  |  | 6000 | 3 | 50 | 250 | 197 | Later | Later | Oil Pump Driven Through Gearbox
65 | 44C-80005C-M1-SH1 | Space Heater for Main Motor | 1 |  | 1 |  | 1 |  |  | 230 |  | 50 | 0.173 | 0.173 | Later | Later
66 | 44C-80005C-M3 | Compressor Ventilation Fan Motor | 1 |  | 1 |  | 1 |  |  | 400 | 3 | 50 | Later | Later | Later | Later
67 | 44C-80005C-M2 | Oil Demister Motor | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 0.37 | 0.37 | Later | Later
68 | 44LCP-8004091 | Compressor LCP | 1 |  | 1 |  | 1 |  |  | 230 | 1 | 50 | 1 | - | - | -
69
70 | Common
71 | 44C-80006A-M1 | Elutriator Fan | 1 |  |  |  | 1 |  |  | 400 | 3 | 50 | 30 | 27.6 | 93.3 | 88.3 | DOL
72 | 44C-80006B-M1 | Elutriator Fan | 1 |  |  |  | 1 |  |  | 400 | 3 | 50 | 30 | 27.6 | 93.3 | 88.3 | DOL
Note ; | 1. Legend ; M : Motor Type Feeder, F : Feed Type (Non Motor), VFD : Motor Type With VFD
2. Legend ; C : Continuous, I : Intermittent, S : Stand-by
1
2