## Resolution Sheet
|  |  |  | PROJECT: | ABT 360 KT/Y PP PLANT Project
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Panel Layout Drawing | 23249-07
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 1 | 0 |  | 1) Following isolated earth bar to be providedISE: for instrinsically safe signalPE: safety earth (electrical and panel body)IE: instrument earth2) one normally close contact shall be considered as digital input , for remote trip command from plant ESD system | 1. Earth bars updated. 2. The current ESD configuration in the UCP expects two constant high (1) signals in order to energize two separate relays. A normally open contact for each of these relays are then wired into the monitoring loop of the ESD relay in the UCP. This loop has to be continuous for the loop to be considered healthy and for the package to not be in a tripped status. This is done to separate the client's system from the UCP's ESD circuit as well as ensuring that if for instance, a cable break occurs, the signal will fall away and cause a trip. In other words, a constant high (1) signal is need from the client's ESD system to keep the package healthy. This is standard practice in all Airpack control systems. Please refer to the wiring diagram for more information.
2
3
4
5
6
7 | [8 empty] | Open
8 | [8 empty] | Closed
9
10
11
12
13
14
15
16
17
18
19
20