## Resolution Sheet
|  |  |  | PROJECT: | ABT 360 KT/Y PP PLANT Project
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Main Motor Data Sheet | L03-RE037-ME-DSH-001 23249-10
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  |  |  | Wouldn't it be more appropriate to use a 4-pole motor and gearbox instead of a 12-pole motor? | The motor is classified as 'A Class Vibration.' A 12-pole motor is preferred for better stability and reduced vibration.
2 |  |  |  | Efficiency:it's very low | It's manufacturer standards.
3 |  |  |  | Power Factor:it's very low | The low power factor is normal for this type of motor because of its inductive nature, which causes a phase difference between voltage and current. This doesn't affect the motor's performance.
4 |  |  |  | space heater to be 230V | It matches the power supply (110 V) available at the site.
5 |  |  |  | One is required for each bearing. | 2 RTDs for the winding are also intended for monitoring the bearings.
6
6 |  |  |  | Voltage&frequency fluctuation to be Specified | updated |  |  |  | Open
7 |  |  |  | RAL 7030 Coating: Verified& Specified | Paint system is 212P, color RAL5015 as per paint procedure. |  |  |  | Closed
8 |  |  |  | Verifying 2years spare part | no 2y spares included. Overall spare parts list will be send after the project.
9
10
11
12
13
14
15
16
17
18
19